## Summary Table
Iowa Energy Efficiency Statewide Technical Reference Manual - Version 3 (Effective Jan. 1, 2019)
Nonresidential High-Impact Measures
Prepared by Vermont Energy Investment Corp.
Code, Title, Programs |  |  |  | Loadshape | Primary Time of Sale Algorithms |  |  |  |  | Primary Early Replacement Algorithms
Measure Code | End Use Category | Measure Title | Applicable Programs | Loadshape(s) | Time of Sale Energy (ΔkWh) | Time of Sale Demand (ΔkW) | Time of Sale Gas (ΔTherms) | Time of Sale Peak Gas (ΔPeakTherms) | Time of Sale Water (ΔGallons) | Existing Unit Life Energy (ΔkWh) | Existing Unit Life Demand (ΔkW) | Existing Unit Life Gas (ΔTherms) | Existing Unit Life Peak Gas (ΔPeakTherms) | Existing Unit Life Water (ΔGallons) | Remaining Life Energy (ΔkWh) | Remaining Life Demand (ΔkW) | Remaining Life Gas (ΔTherms) | Remaining Life Peak Gas (ΔPeakTherms) | Remaining Life Water (ΔGallons) | Sub Algorithms?
NR-AGE-CIRC-V02-180101 | Agricultural Equipment | Circulation Fans | TOS | Loadshape NREV06-Industrial Ventilation | ∆kWh=(WattsBase-WattsEE)/1000* Hours* Nfans | ∆kW=(WattsBase-WattsEE)/1000* CF* Nfans | [13 empty] | No
NR-AGE-VENT-V02-180101 | Agricultural Equipment | Ventilation Fans | TOS | Loadshape NREV06-Industrial Ventilation | ∆kWh=(WattsBase-WattsEE)/1000* hours* Nfans | ∆kW=(WattsBase-WattsEE)/1000* CF* Nfans | [13 empty] | No
NR-AGE-HVLS-V02-180101 | Agricultural Equipment | High Volume Low Speed Fans | RF, NC | Loadshape– NREV06-Industrial Ventilation | ∆kWh=(∑▒〖(¬ N_base*WattsBase)〗-∑▒〖(N_ee*WattsEE)〗)/1000* Hours | ∆kW=(∑▒〖(¬ N_base*WattsBase)〗-∑▒〖(N_ee*WattsEE)〗)/1000* CF | [13 empty] | No
NR-AGE-VCON-V01-170101 | Agricultural Equipment | Temperature Based On/Off Ventilation Controller | RF | Loadshape NREV06-Industrial Ventilation | ∆kWh=(Watts_fan)/1000* (Hours_control ) | [14 empty] | No
NR-HWE-LFFA-V02-190101 | Hot Water | Low Flow Faucet Aerators | DI | Loadshape NREW01:16 - Nonresidential Electric Hot Water (by Building Type) Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type) | ΔkWh = %ElectricDHW * (GPM_base - GPM_low)/(GPM_base) * Usage * EPG_electric * ISR | ΔkW = (ΔkWh )/Hours * CF | ΔTherms = %FossilDHW * (GPM_base - GPM_low)/(GPM_base) * Usage * EPG_gas * ISR | ΔPeakTherms= ΔTherms/365.25 | ΔGallons = (GPM_base - GPM_low)/(GPM_base) * Usage * ISR | [10 empty] | Yes
NR-HWE-LFSH-V03-190101 | Hot Water | Low Flow Showerheads | DI | Loadshape NREW01:16 - Nonresidential Electric Hot Water (by Building Type) Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type) | ΔkWh = %ElectricDHW * ((GPM_base - GPM_low) * L * SPD * Days ) * EPG_electric * ISR | ΔkW = ΔkWh/Hours * CF | ΔTherms = %FossilDHW * (GPM_base- GPM_low) * L* SPD * Days * EPG_gas * ISR | ΔPeakTherms= ΔTherms/365.25 | ΔGallons = (GPM_base - GPM_low ) * L* SPD * Days * ISR | [10 empty] | Yes
NR-HWE-GHWH-V03-190101 | Hot Water | Gas Hot Water Heater | TOS, NC, RF | Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type) |  |  | ∆Therms= ∆Therms_Unit+ ∆Therms _Standby | ΔPeakTherms= (ΔTherms )/365.25 | [11 empty] | Yes
NR-HVC-BOIL-V02-180101 | Heating, Ventilation and Air Conditioning (HVAC) | Boiler | TOS | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NRGB01:16 – Nonresidential Gas Heat and Hot Water (by Building Type) |  |  | ∆THERMS=(EFLH*CAPACITY*((EFFICIENCYRATING (EE))/EFFICIENCYRATING(BASE) -1))/100,000 | ΔPeakTherms= ΔTherms * GCF | [11 empty] | No
NR-HVC-FRNC-V03-190101 | Heating, Ventilation and Air Conditioning (HVAC) | Furnace | TOS | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) |  |  | ∆Therms=(EFLH*Capacity*(〖AFUE〗_eff/〖AFUE〗_base -1))/100,000 | ΔPeakTherms= ΔTherms * GCF | [11 empty] | No
NR-HVC-BLRT-V01-170101 | Heating, Ventilation and Air Conditioning (HVAC) | Boiler Tune-up | RF | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NRGB01:16 – Nonresidential Gas Heat and Hot Water (by Building Type) |  |  | ΔTherms = (Capacity * EFLH *(((Effbefore + Ei))/Effbefore – 1))/100,000 | ΔPeakTherms= ΔTherms * GCF | [11 empty] | No
NR-HVC-FTUN-V02-190101 | Heating, Ventilation and Air Conditioning (HVAC) | Furnace Tune-Up | RF | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NREH01:16 – Nonresidential Electric Heating (by Building Type) | ΔkWh= ΔTherms * Fe * 29.3 |  | ΔTherms = (Capacity * EFLH * (((Effbefore + Ei))/Effbefore – 1) )/100,000 | ΔPeakTherms= ΔTherms * GCF | [11 empty] | No
NR-HVC-GSHP-V02-180101 | Heating, Ventilation and Air Conditioning (HVAC) | Geothermal Source Heat Pump | TOS, NC | Loadshape NREP01:16 - Nonresidential Electric Heat Pump (by Building Type) | ΔkWh = [Cooling savings] + [Heating savings] | ΔkW = ((〖Capacity〗_Cool * (1/〖EER〗_base - 1/〖EER〗_(EE-FL) ))/1000) * CF | [13 empty] | Yes
NR-HVC-PROG-V02-180101 | Heating, Ventilation and Air Conditioning (HVAC) | Small Commercial Programmable Thermostats | RF, DI | Loadshape NREC17 – Non-Residential Cooling – Small Programmable Thermostat Loadshape NREP01:16 – Non-Residential Electric Heat Pump (by Building Type) Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) | ΔkWh = ∆kWh_cooling + ∆kWh_heating |  | ∆Therms = (Sqft * Savings Factor_heat)/(100 * EfficiencyRating(exist)_heat) | ΔPeakTherms= ΔTherms * GCF | [11 empty] | Yes
NR-HVC-VFHP-V02-180101 | Heating, Ventilation and Air Conditioning (HVAC) | Variable Frequency Drives for HVAC Pumps | TOS, RF | Loadshape NRE07 – VFD - Boiler feedwater pumps Loadshape NRE08 – VFD - Chilled water pumps Loadshape NRE09 – VFD - Boiler circulation pumps
NR-HVC-VFDF-V02-190101 | Heating, Ventilation and Air Conditioning (HVAC) | Variable Frequency Drives for HVAC Supply and Return Fans | TOS, RF | Loadshape NRE04 – VFD - Supply fans Loadshape NRE05 – VFD - Return fans Loadshape NRE06 – VFD - Exhaust fans | ΔkWh =([kWh_Base]-[kWh_Retrofit]) *(1+[IE_energy]) | ΔkW =([kW_Base]-[kW_Retrofit]) *(1+[IE_demand])
NR-LTG-STCFL-V02-180101 | Lighting | Compact Fluorescent Lamp - Standard | TOS, DI, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* Hours *WHFe*ISR) * MidLifeAdj | ΔkW = ((〖Watts〗_Base-〖Watts〗_EE)/1,000 * WHFd*CF*ISR) * MidLifeAdj | ΔTherms = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)) * MidLifeAdj | ΔPeakTherms= ΔTherms/HeatDays | [11 empty] | Yes
NR-LTG-SPCFL-V02-180101 | Lighting | Compact Fluorescent Lamp - Specialty | TOS, RF, DI | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* Hours *WHFe*ISR) * MidLifeAdj | ΔkW = ((〖Watts〗_Base-〖Watts〗_EE)/1,000 * WHFd*CF*ISR) * MidLifeAdj | ΔTherms = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)) * MidLifeAdj | ΔPeakTherms= ΔTherms/HeatDays | [11 empty] | Yes
NR-LTG-LEDA-V03-190101 | Lighting | LED Lamp Standard | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* Hours *WHFe*ISR) * MidLifeAdj | ΔkW = ((〖Watts〗_Base-〖Watts〗_EE)/1,000 * WHFd*CF*ISR) * MidLifeAdj | ΔTherms = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)) * MidLifeAdj | ΔPeakTherms= ΔTherms/HeatDays | [11 empty] | Yes
NR-LTG-LEDS-V03-190101 | Lighting | LED Lamp Specialty | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* Hours *WHFe*ISR) * MidLifeAdj | ΔkW = ((〖Watts〗_Base-〖Watts〗_EE)/1,000 * WHFd*CF*ISR) * MidLifeAdj | ΔTherms = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)) * MidLifeAdj | ΔPeakTherms= ΔTherms/HeatDays | [11 empty] | Yes
NR-LTG-T5HO-V01-170101 | Lighting | T5 HO Fixtures and Lamp/Ballast Systems | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* Hours *WHFe*ISR) * MidLifeAdj | ΔkW = ((〖Watts〗_Base-〖Watts〗_EE)/1,000 * WHFd*CF*ISR) * MidLifeAdj | ΔTherms = ((〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)) * MidLifeAdj | ΔPeakTherms= ΔTherms/Heatdays | [11 empty] | Yes
NR-LTG-HPT8-V01-170101 | Lighting | High Performance and Reduced Wattage T8 Fixtures and Lamps | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh =(〖Watts〗_Base-〖Watts〗_EE)/1,000 * Hours *WHFe*ISR*MidLifeAdj | ΔkW =(〖Watts〗_Base-〖Watts〗_EE)/1,000 *ISR * WHFd*CF*MidLifeAdj | ΔTherms = (〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)*MidLifeAdj | ΔPeakTherms= ΔTherms/Heatdays | [11 empty] | Yes
NR-LTG-LDFX-V03-190101 | Lighting | LED Fixtures | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh =(〖Watts〗_Base-〖Watts〗_EE)/1,000 * Hours *WHFe*ISR*MidLifeAdj | ΔkW =(〖Watts〗_Base-〖Watts〗_EE)/1,000 *ISR * WHFd*CF*MidLifeAdj | ΔTherms = (〖Watts〗_Base-〖Watts〗_EE)/1,000* ISR * Hours *(- IFTherms)*MidLifeAdj | ΔPeakTherms= ΔTherms/Heatdays | [11 empty] | Yes
NR-LTG-OSLC-V02-180101 | Lighting | Occupancy Sensor | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type) | ΔkWh = 〖kW〗_Controlled* Hours * ESF * WHFe | ΔkW = 〖kW〗_Controlled* WHFd * (CFbaseline – CFos) | ΔTherms = 〖kW〗_Controlled* Hours * ESF * - IFTherms | ΔPeakTherms= ΔTherms/Heatdays | [11 empty] | Yes
NR-MSC-VFDP-V02-180101 | Miscellaneous | Variable Frequency Drives for Process | TOS, RF | Custom Loadshape | ∆kWh= HP*Hours*SF | [14 empty] | No

## BLANK
BLANK
Measure Code:
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition

## Circulation Fans
Circulation Fans
| Measure Code: | NR-AGE-CIRC-V02-180101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
16
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Install Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Fan Diameter | 12-23 | Actual - $375
|  |  |  | 24-35 | Actual - $450
|  |  |  | 36-47 | Actual - $525
|  |  |  | 48+ | Actual - $600
|  | Unknown |  |  | 150
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / 1000 * [Hours] * [Nfans]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / 1000 * [CF] * [ Nfans]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Fan Diameter | 12-23 |  |  | 366 | N | Watts | Demand (W) of baseline fan
|  |  | 24-35 |  |  | 615
|  |  | 36-47 |  |  | 810
|  |  | 48+ |  |  | 1358
| [WattsEE] | Fan Diameter | 12-23 |  |  | 298 | N | Watts | Demand (W) of efficient fan
|  |  | 24-35 |  |  | 440
|  |  | 36-47 |  |  | 529
|  |  | 48+ |  |  | 993
| [Hours] | Facility Type | Hog |  |  | 3597 | Y | Hours | Actual hours of operation. Typically the fans will be operated above certain temperature thresholds, and therefore the operating hours can be reasonably estimated using the Ag Ventilation Operating Hours Calculator if temperature setpoints are known. If not, the following table can be used to establish operating hours by facility type (hog or dairy). For dairy facilities the typical temperature setpoint can be assumed to be 70⁰F, and for hog facilities it can be assumed to be 60⁰F, as these are the recommended temperatures above which comfort cooling should be provided for livestock .
|  |  | Dairy |  |  | 2099
| [Nfans] | [5 empty] | Y |  | Number of circulation fans
| [CF] |  |  |  |  | 100% | N |  | Summer Peak Coincidence Factor

## Ventilation Fans
Ventilation Fans
| Measure Code: | NR-AGE-VENT-V02-180101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
16
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Install Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Fan Diameter | 12-23 | Actual - $375
|  |  |  | 24-35 | Actual - $450
|  |  |  | 36-47 | Actual - $525
|  |  |  | 48+ | Actual - $600
|  | Unknown |  |  | 150
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / 1000 * [Hours] * [Nfans]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / 1000 * [CF] * [ Nfans]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Fan Diameter | 14-23 |  |  | 382 | N | Watts | Demand (W) of baseline fan
|  |  | 24-35 |  |  | 550
|  |  | 36-47 |  |  | 879
|  |  | 48+ |  |  | 1353
| [WattsEE] | Fan Diameter | 14-23 |  |  | 304 | N | Watts | Demand (W) of efficient fan
|  |  | 24-35 |  |  | 383
|  |  | 36-47 |  |  | 565
|  |  | 48+ |  |  | 1041
| [Hours] | Facility Type | Hog |  |  | 4923 | Y | Hours | Actual hours of operation. Typically the fans will be operated in a staged fashion such that only a fraction of total fans are operating in conditions that do not require maximum installed capacity. Accordingly, effective full load hours (EFLH) should be determined based on operating schedule and considering factors such as number of fans, stages, and temperature band definitions. If this information is unavailable, the table below may be used to reasonably estimate EFLH for hog and dairy facilities, based on typical control schedules
|  |  | Dairy |  |  | 4205
| [Nfans] | [5 empty] | Y |  | Number of circulation fans
| [CF] |  |  |  |  | 100% | N |  | Summer Peak Coincidence Factor

## High Volume Low Speed Fans
High Volume Low Speed Fans
| Measure Code: | NR-AGE-HVLS-V02-180101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
16
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Install Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Fan Diameter | 16-17.9 | Actual - $1,210 | Actual
|  |  |  | 18-19.9 | Actual - $1,460
|  |  |  | 20-23.9 | Actual - $1,840
|  |  |  | 24+ | Actual - $2,090
|  | Unknown | Fan Diameter | 16-17.9 | 4100
|  |  |  | 18-19.9 | 4130
|  |  |  | 20-23.9 | 4190
|  |  |  | 24+ | 4230
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(∑ ([N_base] * [WattsBase]) - ∑([N_ee] *[WattsEE])) / 1000 * [Hours]
| Time of Sale Demand (ΔkW) | =(∑([N_base] * [WattsBase])-∑([N_ee] * [WattsEE)])/1000 * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Nbase] | Retrofit |  |  |  |  | Y |  | Number of baseline (conventional) fans being replaced (of equivalent wattage)
New Construction
| [Wattsbase] | Project Type | New Construction | Diameter of Fan (ft) | 16-17.9 | 4497 | Y | Watts | Operating demand (W) of baseline fan
[5 empty] | 18-19.9 | 5026
[5 empty] | 20-23.9 | 5555
[5 empty] | 24+ | 6613
Retrofit
| [Nee] | [5 empty] | Y |  | Number of efficient fans installed (of equivalent wattage)
| [Wattsee] | Diameter of Fan | 16-17.9 | Type | New Construction | 761 | Y | Watts | Operating demand (W) of efficient fan
|  |  | 18-19.9 |  |  | 850
|  |  | 20-23.9 |  |  | 940
|  |  | 24+ |  |  | 1119
Retrofit
| [Hours] | Facility Type | Hog |  |  | 3597 | Y | Hours | Actual hours of operation. Typically the fans will be operated above certain temperature thresholds, and therefore the operating hours can be reasonably estimated using the Ag Ventilation Operating Hours Calculator if temperature setpoints are known. If not, the following table can be used to establish operating hours. For dairy facilities the typical temperature setpoint can be assumed to be 70⁰F, and for hog facilities it can be assumed to be 60⁰F, as these are the recommended temperatures above which comfort cooling should be provided for livestock.
|  |  | Dairy |  |  | 2099
| [CF] |  |  |  |  | 100% | N |  | Summer Peak Coincidence Factor

## Temp. Based On Off Vent. Contr.
Temp. Based On Off Vent. Contr.
| Measure Code: | NR-AGE-VCON-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
7
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([Watts_fan]) / 1000 * ([Hours_control] )
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Watts_fan] | Diamter of Fan | 14-23 |  |  | 382 | Y | Watts | Total wattage of controlled fans
|  |  | 24-35 |  |  | 550
|  |  | 36-47 |  |  | 879
|  |  | 48+ |  |  | 1353
| [Hourscontrol] | Facility Type | Hog |  |  | 1384 | N | Hours | Reduction in fan run hours due to controller
|  |  | Dairy |  |  | 624

## Low Flow Faucet Aerators
Low Flow Faucet Aerators
| Measure Code: | NR-HWE-LFFA-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
9
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Actual
|  | Unknown | 16
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [%ElectricDHW] * ([GPM_base] - [GPM_low]) / ([GPM_base]) * [Usage] * [EPG_electric] * [ISR]
| Time of Sale Demand (ΔkW) | = ([ΔkWh]) / [Hours] * [CF]
| Time of Sale Gas (ΔTherms) | = [%FossilDHW] * ([GPM_base] - [GPM_low]) / ([GPM_base]) * [Usage] * [EPG_gas] * [ISR]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [365.25]
| Time of Sale Water (ΔGallons) | = ([GPM_base] - [GPM_low]) / ([GPM_base]) * [Usage] * [ISR]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [GPM_base] |  |  | = [Measured full throttle flow] * [0.83]
| [GPM_low] |  |  | =[Rated full throttle flow] * [0.95]
| [EPG_electric] |  |  | = ([γWater] * [1.0] * ([WaterTemp] - [SupplyTemp])) / ([RE_electric] * [3412])
| [Hours] |  |  | = ([Usage] * [0.479] )/ [GPH]
| [EPG_gas] |  |  | = ([8.33] * [1.0] * ([WaterTemp] - [SupplyTemp])) / ([RE_gas] * [100,000])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [%ElectricDHW] | Fuel Type | Electric |  |  | 100% | N |  | Proportion of water heating supplied by electric resistance heating
|  |  | Fossil Fuel |  |  | 0%
|  |  | Unknown |  |  | 53%
| [GPM_base] |  |  |  |  | 1.83 | C | GMP | Average flow rate, in gallons per minute, of the baseline faucet "as-used"
| [Measured full throttle flow] | [5 empty] | Y | GPM | Measured Full Throttle Flow of baseline faucet
| [0.83] | [5 empty] | N |  | Base faucet throttling factor
| [GPM_low] |  |  |  |  | 1.43 | C | GPM | Average flow rate, in gallons per minute, of the low-flow faucet aerator "as-used". Default when flow not measured assumes 1.5 GPM flow.
| [Rated full throttle flow] | [5 empty] | Y | GPM | Rated Full Throttle Flow of low-flow faucet
| [0.95] | [5 empty] | N |  | Low flow faucet throttling factor
| [Usage] | Building Type | Small Office |  |  | 2500 | Y | Gallons | Estimated usage of mixed water (mixture of hot water from water heater line and cold water line) per faucet
|  |  | Large Office |  |  | 11250
|  |  | Fast Food Rest. |  |  | 9588
|  |  | Sit-Down Rest. |  |  | 15779
|  |  | Retail |  |  | 3653
|  |  | Grocery |  |  | 3653
|  |  | Warehouse |  |  | 2500
|  |  | Elementary School |  |  | 3000
|  |  | Jr/Sr High School |  |  | 9000
|  |  | Health |  |  | 16436
|  |  | Motel |  |  | 1826
|  |  | Hotel |  |  | 1278
|  |  | Other |  |  | 5000
| [EPG_electric] | Water Heater Type | Resistane Tank or Unknown |  |  | 0.0822 | C | kWh/gal | Energy per gallon of mixed water used by faucet (electric water heater)
|  |  | Heat Pump Water Tank |  |  | 0.0288
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight of water
| [1.0] |  |  |  |  | 1 | N | Btu/lb-°F | Heat Capacity of water
| [WaterTemp] | Location | Bath |  |  | 86 | N | °F | Assumed temperature of mixed water
|  |  | Kitchen |  |  | 93
| [SupplyTemp] |  |  |  |  | 56.5 | N | °F | Assumed temperature of water entering building
| [RE_electric] | Water Heater Type | Electric Resistance (or unknown) |  |  | 98% | N | Percentage | Recovery efficiency of electric water heater
|  |  | Heat Pump Water Heaters |  |  | 280%
| [3412] |  |  |  |  | 3412 | N | Btu/kWh | Converts Bto to kWh
| [ISR] |  |  |  |  | 1 | N |  | In service rate of faucet aerators
| [ΔkWh] | DHW Type | Resistance Tank | Building Type | Small Office | 44.9 | C | kWh | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 202.2
[5 empty] | Fast Food Rest. | 172.3
[5 empty] | Sit-Down Rest. | 283.5
[5 empty] | Retail | 65.6
[5 empty] | Grocery | 65.6
[5 empty] | Warehouse | 44.9
[5 empty] | Elementary School | 53.9
[5 empty] | Jr/Sr High School | 161.7
[5 empty] | Health | 295.3
[5 empty] | Motel | 32.8
[5 empty] | Hotel | 23
[5 empty] | Other | 89.8
|  |  | Heat Pump Tank | Building Type | Small Office | 15.7
[5 empty] | Large Office | 70.8
[5 empty] | Fast Food Rest. | 60.3
[5 empty] | Sit-Down Rest. | 99.2
[5 empty] | Retail | 23
[5 empty] | Grocery | 23
[5 empty] | Warehouse | 15.7
[5 empty] | Elementary School | 18.9
[5 empty] | Jr/Sr High School | 56.6
[5 empty] | Health | 103.4
[5 empty] | Motel | 11.5
[5 empty] | Hotel | 8
[5 empty] | Other | 31.4
|  |  | Unknown DHW | Building Type | Small Office | 23.8
[5 empty] | Large Office | 107.1
[5 empty] | Fast Food Rest. | 91.3
[5 empty] | Sit-Down Rest. | 150.3
[5 empty] | Retail | 34.8
[5 empty] | Grocery | 34.8
[5 empty] | Warehouse | 23.8
[5 empty] | Elementary School | 28.6
[5 empty] | Jr/Sr High School | 85.7
[5 empty] | Health | 156.5
[5 empty] | Motel | 17.4
[5 empty] | Hotel | 12.2
[5 empty] | Other | 47.6
| [Hours] | Building Type | Small Office | Tank Type | Resistance | 17.4 | C | Hours | Annual electric DHW recovery hours for faucet use. Values based on defaults above.
|  |  | Large Office |  |  | 78.3
|  |  | Fast Food Rest. |  |  | 66.7
|  |  | Sit-Down Rest. |  |  | 109.8
|  |  | Retail |  |  | 25.4
|  |  | Grocery |  |  | 25.4
|  |  | Warehouse |  |  | 17.4
|  |  | Elementary School |  |  | 20.9
|  |  | Jr/Sr High School |  |  | 62.7
|  |  | Health |  |  | 114.4
|  |  | Motel |  |  | 12.7
|  |  | Hotel |  |  | 8.9
|  |  | Other |  |  | 34.8
|  |  | Small Office |  | Heat Pump | 6.1
|  |  | Large Office |  |  | 27.4
|  |  | Fast Food Rest. |  |  | 23.3
|  |  | Sit-Down Rest. |  |  | 38.4
|  |  | Retail |  |  | 8.9
|  |  | Grocery |  |  | 8.9
|  |  | Warehouse |  |  | 6.1
|  |  | Elementary School |  |  | 7.3
|  |  | Jr/Sr High School |  |  | 21.9
|  |  | Health |  |  | 40
|  |  | Motel |  |  | 4.4
|  |  | Hotel |  |  | 3.1
|  |  | Other |  |  | 12.2
| [GPH] | Water Heater Type | Resistance |  |  | 68.8 | N | gal/hour | Gallons per hour recovery of electric water heater calculated for 70F temp rise (126.5-56.5), 98% for resistance (or unknown) or 280% for heat pump water tanks recovery efficiency, and typical 12kW electric resistance storage tank
|  |  | Heat Pump |  |  | 196.6
| [CF] | Building Type | Small Office | Tank Type | Resistance | 0.0045 | N |  | Coincidence Factor for electric load reduction
|  |  | Large Office |  |  | 0.0238
|  |  | Fast Food Rest. |  |  | 0.0114
|  |  | Sit-Down Rest. |  |  | 0.025
|  |  | Retail |  |  | 0.0058
|  |  | Grocery |  |  | 0.0058
|  |  | Warehouse |  |  | 0.006
|  |  | Elementary School |  |  | 0.0054
|  |  | Jr/Sr High School |  |  | 0.0161
|  |  | Health |  |  | 0.0196
|  |  | Motel |  |  | 0.0009
|  |  | Hotel |  |  | 0.0006
|  |  | Other |  |  | 0.0119
|  |  | Small Office |  | Heat Pump | 0.0016
|  |  | Large Office |  |  | 0.0083
|  |  | Fast Food Rest. |  |  | 0.004
|  |  | Sit-Down Rest. |  |  | 0.0088
|  |  | Retail |  |  | 0.002
|  |  | Grocery |  |  | 0.002
|  |  | Warehouse |  |  | 0.00211
|  |  | Elementary School |  |  | 0.0019
|  |  | Jr/Sr High School |  |  | 0.0056
|  |  | Health |  |  | 0.0069
|  |  | Motel |  |  | 0.0003
|  |  | Hotel |  |  | 0.0002
|  |  | Other |  |  | 0.0042
| [ΔkW] | DHW Type | Resistance Tank | Building Type | Small Office | 0.0115 | C | kW | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 0.0615
[5 empty] | Fast Food Rest. | 0.0295
[5 empty] | Sit-Down Rest. | 0.0647
[5 empty] | Retail | 0.015
[5 empty] | Grocery | 0.015
[5 empty] | Warehouse | 0.0154
[5 empty] | Elementary School | 0.0138
[5 empty] | Jr/Sr High School | 0.0415
[5 empty] | Health | 0.0505
[5 empty] | Motel | 0.0022
[5 empty] | Hotel | 0.0016
[5 empty] | Other | 0.0308
|  |  | Heat Pump Tank | Building Type | Small Office | 0.004
[5 empty] | Large Office | 0.0215
[5 empty] | Fast Food Rest. | 0.0103
[5 empty] | Sit-Down Rest. | 0.0226
[5 empty] | Retail | 0.0052
[5 empty] | Grocery | 0.0052
[5 empty] | Warehouse | 0.0054
[5 empty] | Elementary School | 0.0048
[5 empty] | Jr/Sr High School | 0.0145
[5 empty] | Health | 0.0177
[5 empty] | Motel | 0.0008
[5 empty] | Hotel | 0.0006
[5 empty] | Other | 0.0108
|  |  | Unknown DHW | Building Type | Small Office | 0.0061
[5 empty] | Large Office | 0.0326
[5 empty] | Fast Food Rest. | 0.0156
[5 empty] | Sit-Down Rest. | 0.0343
[5 empty] | Retail | 0.0079
[5 empty] | Grocery | 0.0079
[5 empty] | Warehouse | 0.0082
[5 empty] | Elementary School | 0.0073
[5 empty] | Jr/Sr High School | 0.022
[5 empty] | Health | 0.0268
[5 empty] | Motel | 0.0012
[5 empty] | Hotel | 0.0008
[5 empty] | Other | 0.0163
| [%FossilDHW] | Fuel Type | Electric |  |  | 0% | N |  | Proportion of water heating supplied by fossil fuel heating
|  |  | Fossil Fuel |  |  | 100%
|  |  | Unknown |  |  | 47%
| [EPG_gas] | Tank Type | Storage Tank |  |  | 0.0035 | C |  | Energy per gallon of mixed water used by faucet (gas water heater)
|  |  | Centrail Boiler |  |  | 0.0047
|  |  | Unknown |  |  | 0.004
| [RE_gas] | Tank Type | Storage Tank |  |  | 78% | N |  | Recovery efficiency of gas water heater
|  |  | Centrail Boiler |  |  | 59%
|  |  | Unknown |  |  | 69%
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | DHW Type | Storage Tank | Building Type | Small Office | 1.9 | C | Therm | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 8.7
[5 empty] | Fast Food Rest. | 7.4
[5 empty] | Sit-Down Rest. | 12.2
[5 empty] | Retail | 2.8
[5 empty] | Grocery | 2.8
[5 empty] | Warehouse | 1.9
[5 empty] | Elementary School | 2.3
[5 empty] | Jr/Sr High School | 6.9
[5 empty] | Health | 12.7
[5 empty] | Motel | 1.4
[5 empty] | Hotel | 1
[5 empty] | Other | 3.9
|  |  | Central Boiler DHW | Building Type | Small Office | 2.5
[5 empty] | Large Office | 11.5
[5 empty] | Fast Food Rest. | 9.8
[5 empty] | Sit-Down Rest. | 16.1
[5 empty] | Retail | 3.7
[5 empty] | Grocery | 3.7
[5 empty] | Warehouse | 2.5
[5 empty] | Elementary School | 3.1
[5 empty] | Jr/Sr High School | 9.2
[5 empty] | Health | 16.7
[5 empty] | Motel | 1.9
[5 empty] | Hotel | 1.3
[5 empty] | Other | 5.1
|  |  | Unknown Gas DHW | Building Type | Small Office | 2.2
[5 empty] | Large Office | 9.8
[5 empty] | Fast Food Rest. | 8.3
[5 empty] | Sit-Down Rest. | 13.7
[5 empty] | Retail | 3.2
[5 empty] | Grocery | 3.2
[5 empty] | Warehouse | 2.2
[5 empty] | Elementary School | 2.6
[5 empty] | Jr/Sr High School | 7.8
[5 empty] | Health | 14.3
[5 empty] | Motel | 1.6
[5 empty] | Hotel | 1.1
[5 empty] | Other | 4.4
|  |  | Unknown DHW | Building Type | Small Office | 1
[5 empty] | Large Office | 4.6
[5 empty] | Fast Food Rest. | 3.9
[5 empty] | Sit-Down Rest. | 6.5
[5 empty] | Retail | 1.5
[5 empty] | Grocery | 1.5
[5 empty] | Warehouse | 1
[5 empty] | Elementary School | 1.2
[5 empty] | Jr/Sr High School | 3.7
[5 empty] | Health | 6.7
[5 empty] | Motel | 0.7
[5 empty] | Hotel | 0.5
[5 empty] | Other | 2
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year
| [ΔPeakTherms] | DHW Type | Storage Tank | Building Type | Small Office | 0.0053 | C | Therm | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 0.0237
[5 empty] | Fast Food Rest. | 0.0202
[5 empty] | Sit-Down Rest. | 0.0333
[5 empty] | Retail | 0.0077
[5 empty] | Grocery | 0.0077
[5 empty] | Warehouse | 0.0053
[5 empty] | Elementary School | 0.0063
[5 empty] | Jr/Sr High School | 0.019
[5 empty] | Health | 0.0346
[5 empty] | Motel | 0.0038
[5 empty] | Hotel | 0.0027
[5 empty] | Other | 0.0105
|  |  | Central Boiler DHW | Building Type | Small Office | 0.007
[5 empty] | Large Office | 0.0314
[5 empty] | Fast Food Rest. | 0.0267
[5 empty] | Sit-Down Rest. | 0.044
[5 empty] | Retail | 0.0102
[5 empty] | Grocery | 0.0102
[5 empty] | Warehouse | 0.007
[5 empty] | Elementary School | 0.0084
[5 empty] | Jr/Sr High School | 0.0251
[5 empty] | Health | 0.0458
[5 empty] | Motel | 0.0051
[5 empty] | Hotel | 0.0036
[5 empty] | Other | 0.0139
|  |  | Unknown Gas DHW | Building Type | Small Office | 0.006
[5 empty] | Large Office | 0.0268
[5 empty] | Fast Food Rest. | 0.0228
[5 empty] | Sit-Down Rest. | 0.0376
[5 empty] | Retail | 0.0087
[5 empty] | Grocery | 0.0087
[5 empty] | Warehouse | 0.006
[5 empty] | Elementary School | 0.0072
[5 empty] | Jr/Sr High School | 0.0215
[5 empty] | Health | 0.0392
[5 empty] | Motel | 0.0044
[5 empty] | Hotel | 0.003
[5 empty] | Other | 0.0119
|  |  | Unknown DHW | Building Type | Small Office | 0.0028
[5 empty] | Large Office | 0.0126
[5 empty] | Fast Food Rest. | 0.0107
[5 empty] | Sit-Down Rest. | 0.0177
[5 empty] | Retail | 0.0041
[5 empty] | Grocery | 0.0041
[5 empty] | Warehouse | 0.0028
[5 empty] | Elementary School | 0.0034
[5 empty] | Jr/Sr High School | 0.0101
[5 empty] | Health | 0.0184
[5 empty] | Motel | 0.002
[5 empty] | Hotel | 0.0014
[5 empty] | Other | 0.0056
| [ΔGallons] | Building Type | Small Office |  |  | 546 | C | Gallons | Calculated value above per faucet basis. Values based on all defaults provided.
|  |  | Large Office |  |  | 2459
|  |  | Fast Food Rest. |  |  | 2094
|  |  | Sit-Down Rest. |  |  | 3447
|  |  | Retail |  |  | 798
|  |  | Grocery |  |  | 798
|  |  | Warehouse |  |  | 546
|  |  | Elementary School |  |  | 656
|  |  | Jr/Sr High School |  |  | 1967
|  |  | Health |  |  | 3590
|  |  | Motel |  |  | 399
|  |  | Hotel |  |  | 279
|  |  | Other |  |  | 1093

## Low Flow Showerheads
Low Flow Showerheads
| Measure Code: | NR-HWE-LFSH-V03-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Actual
|  | Unknown | 20
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [%ElectricDHW] * (([GPM_base] - [GPM_low]) * [L * SPD * Days] ) * [EPG_electric] * [ISR]
| Time of Sale Demand (ΔkW) | = [ΔkWh] / [Hours] * [CF]
| Time of Sale Gas (ΔTherms) | = [%FossilDHW] * ([GPM_base] - [GPM_low]) * [L * SPD * Days] * [EPG_gas] * [ISR]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [365.25]
| Time of Sale Water (ΔGallons) | = ([GPM_base] - [GPM_low] ) *[L * SPD * Days] * [ISR]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [(L * SPD * Days)] |  |  | =[(L * SPD * Days)]
| [EPG_electric] |  |  | = ([γWater] * [1.0] * ([ShowerTemp] - [SupplyTemp])) / ([RE_electric] * [3412])
| [Hours] |  |  | = ([GPM_base] *[L] * [SPD] * [365.25] * [0.65] )/ [GPH]
| [EPG_gas] |  |  | = ([8.33] * [1.0] * ([ShowerTemp] - [SupplyTemp])) / ([RE_gas] * [100,000])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [%ElectricDHW] | Fuel Type | Electric |  |  | 100% | N |  | Proportion of water heating supplied by electric resistance heating
|  |  | Fossil Fuel |  |  | 0%
|  |  | Unknown |  |  | 53%
| [GPM_base] |  |  |  |  | 2.5 | Y | GPM | Flow rate of the baseline showerhead
| [GPM_low] |  |  |  |  | 1.5 | Y | GPM | Flow rate of the low-flow showerhead
| [(L * SPD * Days)] | Building Type | Hospitality |  |  | 3509 | C | Minutes | Minutes of use per showerhead annually. Ideally apply the custom calculation. If not possible use defaults provided.
|  |  | Health |  |  | 2528
|  |  | Commercial – Employee Shower |  |  | 1894
|  |  | Education |  |  | 2057
|  |  | Other Commercial Except Fitness Center |  |  | 3029
|  |  | Fitness Center |  |  | 56893
| [L] |  |  |  |  | 7.8 | Y | Minutes | Shower length in minutes with showerhead
| [SPD] | [5 empty] | Y |  | Showers Per Day for showerhead
| [Days] | [5 empty] | Y | days | Days per year, on average
| [EPG_electric] | Water Heater Type | Resistance or unknown |  |  | 0.1109 | C |  | Energy per gallon of hot water supplied by electric
|  |  | Heat Pump |  |  | 0.0543
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight of water
| [1.0] |  |  |  |  | 1 | N | Btu/lb-°F | Heat Capacity of water
| [ShowerTemp] |  |  |  |  | 101 | N | °F | Assumed temperature of water
| [SupplyTemp] |  |  |  |  | 56.5 | N | °F | Assuned tenperature of water entering house
| [RE_electric] | Water Heater Type | Electric Resistance (or unknown) |  |  | 98% | N |  | Average recovery efficiency of electric water heater
|  |  | Heat Pump Water Heaters |  |  | 200%
| [3412] |  |  |  |  | 3412 | N | Btu/kWh | Converts Bto to kWh
| [ISR] |  |  |  |  | 1 | N |  | In service rate of showerheads
| [ΔkWh] | [5 empty] | C | kWh | calculated value above per faucet basis
| [Hours] | [5 empty] | C | Hours | Annual electric DHW recovery hours for showerhead use
| [GPH] | Water Heater Type | Resistance |  |  | 68.8 | N | gal/hour | Gallons per hour recovery of electric water heater calculated for 70F temp rise (126.5-56.5), 98% recovery efficiency for electric resistance (or unknown) and 200% for heat pump water heaters, and typical 12kW electric resistance storage tank
|  |  | Heat Pump |  |  | 140.4
| [CF] |  |  |  |  | 1.6% | N |  | Coincidence Factor for electric load reduction
| [%FossilDHW] | Fuel Type | Electric |  |  | 0% | N |  | Proportion of water heating supplied by fossil fuel heating
|  |  | Fossil Fuel |  |  | 100%
|  |  | Unknown |  |  | 47%
| [EPG_gas] | Tank Type | Storage Tank |  |  | 0.0048 | C |  | Energy per gallon of Hot water supplied by gas
|  |  | Centrail Boiler |  |  | 0.0063
|  |  | Unknown |  |  | 0.0054
| [RE_gas] | Tank Type | Storage Tank |  |  | 78% | N |  | Recovery efficiency of gas water heater
|  |  | Centrail Boiler |  |  | 59%
|  |  | Unknown |  |  | 69%
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year

## Gas Hot Water Heater
Gas Hot Water Heater
| Measure Code: | NR-HWE-GHWH-V03-190101
| Lifetime of Efficient Equipment: | [8 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [6 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Water Heater Type | Storage Tank | 15
|  | Tankless | 20
| Measure Cost: | [8 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Incremental Install Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  |  |  | Actual | Actual
|  | Unknown | Equipment Type | Gas Storage Water Heaters ≤ 75,000 Btu/h, ≤55 Gallons | Category | Baseline | N/A | 616
[6 empty] | Efficient | 440 | 1055
|  |  |  | Gas Storage Water Heaters > 75,000 Btu/h |  | 0.80 Et | N/A | 4886
[6 empty] | 0.83 Et | 220 | 5106
[6 empty] | 0.84 Et | 413 | 5299
[6 empty] | 0.85 Et | 529 | 5415
[6 empty] | 0.86 Et | 646 | 5532
[6 empty] | 0.87 Et | 762 | 5648
[6 empty] | 0.88 Et | 879 | 5765
[6 empty] | 0.89 Et | 996 | 5882
[6 empty] | 0.90 Et | 1135 | 6021
|  |  |  | Gas Tankless Water Heaters >50,000 Btu/h and <200,000 Btu/h |  | Tankless Baseline | N/A | 593
[6 empty] | Efficient | 487 | 1080
[6 empty] | Incremental using Storage Baseline | 465
|  |  |  | Gas Tankless Water Heaters ≥200,000 Btu/h |  | Tankless Baseline | N/A | 1148
[6 empty] | Efficient | 278 | 1427
[6 empty] | Incremental using Storage Baseline | -3459
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
| Tank type | Gas fired tankless | 1 | 100
|  | All other | N/A | N/A
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = [∆Therms_Unit] + [∆Therms_Standby]
| Time of Sale Peak Gas (ΔPeakTherms) | = ([ΔTherms] ) / [365.25]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Sub Algorithm
| [∆Therms_Unit] |  |  |  |  | = (([T_out] - [T_in] ) * [HotWaterUse_Gallon] * [γWater] * [1 ] * (1/ [EF_base] - 1/[EF_Eff ]) / [100,000])
| [HotWaterUseGallon] | Method of estimation | Actual |  |  | Actual
|  |  | Water Heater Capacity |  |  | = [Capacity] * [Consumption/cap]
|  |  | Facility Size |  |  | = [Area]/1000 * [Consumption/1000 sq. ft.]
| [Efbase] | Equipment Type | Gas Storage ≤ 75,000 Btu/h | Size Category | ≤55 gallon tanks | 0.675 – (0.0015 * [Rated Storage Volume])
[5 empty] | >55 gallon tanks | 0.8012 – (0.00078 * [Rated Storage Volume])
|  |  | Gas Storage > 75,000 Btu/h |  | < 4000 Btu/h/gal | 80%
|  |  | Gas Tankless >50,000 Btu/h and <200,000 Btu/h |  | < 4000 Btu/h/gal and <2 gal tank | 0.82 – (0.0019 * [Rated Storage Volume])
|  |  | Gas Tankless ≥200,000 Btu/h |  | ≥ 4000 Btu/h/gal and <10 gal tank | 80%
|  |  | Gas Tankless ≥200,000 Btu/h |  | ≥ 4000 Btu/h/gal and ≥10 gal tank | 80%
| [∆Therms_Standby] | Water heater type and size | Gas Storage >75,000 Btu/h |  |  | =([SL_base] - [SL_eff]) * [8766]) / [100,000]
Gas Tankless ≥200,000 Btu/h and with ≥10gal tank
|  |  | All other |  |  | 0
| [SLbase] |  |  |  |  | = [Q]/800 + 110√[V]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Tout] |  |  |  |  | 140 | Y | °F | Unmixed Outlet Water Temperature
| [Tin] |  |  |  |  | 56.5 | Y | °F | Inlet Water Temperature
| [HotWaterUseGallon] | [5 empty] | C | Gallons | Estimated annual hot water consumption
| [Consumption/cap] | Building Type | Convenience |  |  | 528 | N | Gallons | Estimate of consumption per gallon of usable tank capacity, dependent on building type
|  |  | Education |  |  | 568
|  |  | Grocery |  |  | 528
|  |  | Health |  |  | 788
|  |  | Large Office |  |  | 511
|  |  | Large Retail |  |  | 528
|  |  | Lodging |  |  | 715
|  |  | Other Commercial |  |  | 341
|  |  | Restaurant |  |  | 377
|  |  | Small Office |  |  | 511
|  |  | Small Retail |  |  | 528
|  |  | Warehouse |  |  | 341
|  |  | Nursing |  |  | 672
|  |  | Multifamily |  |  | 894
| [Capacity] | [5 empty] | Y |  | Usable capacity of hot water storage tank in gallons
| [Area] | [5 empty] | Y |  | Area in sq. ft. that is served by DHW boiler
| [Consumption/1000 sq. ft.] | Building Type | Convenience |  |  | 3634 | N | Gallons | Estimate of DHW consumption (gallons) per 1000 ft2 of floor area
|  |  | Education |  |  | 5440
|  |  | Grocery |  |  | 1150
|  |  | Health |  |  | 13663
|  |  | Large Office |  |  | 1205
|  |  | Large Retail |  |  | 157
|  |  | Lodging |  |  | 18541
|  |  | Other Commercial |  |  | 3573
|  |  | Restaurant |  |  | 26927
|  |  | Small Office |  |  | 931
|  |  | Small Retail |  |  | 913
|  |  | Warehouse |  |  | 476
|  |  | Nursing |  |  | 26721
|  |  | Multifamily |  |  | 13133
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight of water
| [1] |  |  |  |  | 1 | N | Btu/lbm/°F | Specific heat of water
| [Efbase] |  |  |  |  | 80% | N |  | Rated thermal efficiency of baseline water heater
| [Efeff] | [5 empty] | Y |  | Rated thermal efficiency of efficient water heater
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [∆Therms_Standby] | [5 empty] | C |  | Additional savings due to lower standby losses
| [SLbase] | [5 empty] | C |  | Standby loss of baseline unit
| [Q] | [5 empty] | Y | Btu/h | Nameplate input rating in Btu/h
| [V] | [5 empty] | Y | Gallons | Rated volume in gallons
| [SLeff] | [5 empty] | Y | Btu/h | Nameplate standy loss of new water rheater in Btu/h
| [8766] | [5 empty] | N | Hours | Hours per year
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year

## Boiler
Boiler
| Measure Code: | NR-HVC-BOIL-V02-180101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
25
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  | Actual - baseline
|  | Unknown | AFUE | 82% | N/A
|  |  |  | 85% | 633
|  |  |  | 86% | 1429
|  |  |  | 87% | 1441
|  |  |  | 88% | 1562
|  |  |  | 89% | 1683
|  |  |  | 90% | 1803
|  |  |  | 91% | 1748
|  |  |  | 92% | 1899
|  |  |  | 93% | 2050
|  |  |  | 94% | 2201
|  |  |  | 95% | 2353
|  |  |  | 96% | 2504
|  |  |  | 97% | 2655
|  |  |  | 98% | 2806
|  |  |  | 99% | 2957
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =([EFLH] * [Capacity] * (([EfficiencyRating (EE)]) / [EfficiencyRating(BASE)] -1)) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLH ] | Building Type | Convenience | Climate Zone | Burlington | 785 | N | Hours | Equivalent Full Load Hours for heating space
|  |  | Education |  |  | 968
|  |  | Grocery |  |  | 511
|  |  | Health |  |  | 1021
|  |  | Hospital |  |  | 906
|  |  | Industrial |  |  | 849
|  |  | Lodging |  |  | 1396
|  |  | Multifamily |  |  | 1396
|  |  | Office - Large |  |  | 1351
|  |  | Office - Small |  |  | 1290
|  |  | Religious |  |  | 1322
|  |  | Restaurant |  |  | 1036
|  |  | Retail - Large |  |  | 893
|  |  | Retail - Small |  |  | 1200
|  |  | Warehouse |  |  | 1205
|  |  | Nonresidential Average |  |  | 1197
|  |  | Convenience |  | Des Moines | 1071
|  |  | Education |  |  | 1300
|  |  | Grocery |  |  | 737
|  |  | Health |  |  | 1413
|  |  | Hospital |  |  | 1073
|  |  | Industrial |  |  | 1183
|  |  | Lodging |  |  | 1703
|  |  | Multifamily |  |  | 1703
|  |  | Office - Large |  |  | 1491
|  |  | Office - Small |  |  | 1495
|  |  | Religious |  |  | 1796
|  |  | Restaurant |  |  | 1247
|  |  | Retail - Large |  |  | 1303
|  |  | Retail - Small |  |  | 1608
|  |  | Warehouse |  |  | 1440
|  |  | Nonresidential Average |  |  | 1497
|  |  | Convenience |  | Mason City | 1224
|  |  | Education |  |  | 1497
|  |  | Grocery |  |  | 963
|  |  | Health |  |  | 1529
|  |  | Hospital |  |  | 1379
|  |  | Industrial |  |  | 1275
|  |  | Lodging |  |  | 1900
|  |  | Multifamily |  |  | 1900
|  |  | Office - Large |  |  | 1616
|  |  | Office - Small |  |  | 1673
|  |  | Religious |  |  | 1873
|  |  | Restaurant |  |  | 1381
|  |  | Retail - Large |  |  | 1394
|  |  | Retail - Small |  |  | 1768
|  |  | Warehouse |  |  | 1627
|  |  | Nonresidential Average |  |  | 1654
| [Capacity] | [5 empty] | Y | Btu/hr | Nominal Heating Input Capacity Boiler size (Btu/hr) for efficient unit not existing unit
| [EfficiencyRating(base)] |  |  |  |  | 82% | N |  | Baseline equiment efficiency rating in Annuel Fuel Utilization Efficiency Rating (AFUE)
| [EfficiencyRating(EE)] | [5 empty] | Y |  | Efficiency equiment efficiency rating in Annuel Fuel Utilization Efficiency Rating (AFUE)
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  | 0.01631 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.013261
|  |  | Grocery |  |  | 0.021811
|  |  | Health |  |  | 0.011071
|  |  | Hospital |  |  | 0.013578
|  |  | Industrial |  |  | 0.01424
|  |  | Lodging |  |  | 0.008752
|  |  | Multifamily |  |  | 0.008752
|  |  | Office - Large |  |  | 0.010094
|  |  | Office - Small |  |  | 0.011695
|  |  | Religious |  |  | 0.011745
|  |  | Restaurant |  |  | 0.01051
|  |  | Retail - Large |  |  | 0.014243
|  |  | Retail - Small |  |  | 0.011861
|  |  | Warehouse |  |  | 0.01201
|  |  | Nonresidential Average |  |  | 0.012

## Furnace
Furnace
| Measure Code: | NR-HVC-FRNC-V03-190101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
18
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  | Actual - Baseline
|  | Unknown | AFUE | 85% | N/A
|  |  |  | 86% | 56
|  |  |  | 87% | 113
|  |  |  | 88% | 169
|  |  |  | 89% | 226
|  |  |  | 90% | 282
|  |  |  | 91% | 339
|  |  |  | 92% | 395
|  |  |  | 93% | 452
|  |  |  | 94% | 508
|  |  |  | 95% | 565
|  |  |  | 96% | 858
|  |  |  | 97% | 1151
|  |  |  | 98% | 1444
|  |  |  | 99% | 1738
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =([EFLH] * [Capacity]* ([AFUE_eff] / [AFUE_base] -[1])) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLH ] | Building Type | Convenience | Climate Zone | Burlington | 785 | N | Hours | Equivalent Full Load Hours for heating space
|  |  | Education |  |  | 968
|  |  | Grocery |  |  | 511
|  |  | Health |  |  | 1021
|  |  | Hospital |  |  | 906
|  |  | Industrial |  |  | 849
|  |  | Lodging |  |  | 1396
|  |  | Multifamily |  |  | 1396
|  |  | Office - Large |  |  | 1351
|  |  | Office - Small |  |  | 1290
|  |  | Religious |  |  | 1322
|  |  | Restaurant |  |  | 1036
|  |  | Retail - Large |  |  | 893
|  |  | Retail - Small |  |  | 1200
|  |  | Warehouse |  |  | 1205
|  |  | Nonresidential Average |  |  | 1197
|  |  | Convenience |  | Des Moines | 1071
|  |  | Education |  |  | 1300
|  |  | Grocery |  |  | 737
|  |  | Health |  |  | 1413
|  |  | Hospital |  |  | 1073
|  |  | Industrial |  |  | 1183
|  |  | Lodging |  |  | 1703
|  |  | Multifamily |  |  | 1703
|  |  | Office - Large |  |  | 1491
|  |  | Office - Small |  |  | 1495
|  |  | Religious |  |  | 1796
|  |  | Restaurant |  |  | 1247
|  |  | Retail - Large |  |  | 1303
|  |  | Retail - Small |  |  | 1608
|  |  | Warehouse |  |  | 1440
|  |  | Nonresidential Average |  |  | 1497
|  |  | Convenience |  | Mason City | 1224
|  |  | Education |  |  | 1497
|  |  | Grocery |  |  | 963
|  |  | Health |  |  | 1529
|  |  | Hospital |  |  | 1379
|  |  | Industrial |  |  | 1275
|  |  | Lodging |  |  | 1900
|  |  | Multifamily |  |  | 1900
|  |  | Office - Large |  |  | 1616
|  |  | Office - Small |  |  | 1673
|  |  | Religious |  |  | 1873
|  |  | Restaurant |  |  | 1381
|  |  | Retail - Large |  |  | 1394
|  |  | Retail - Small |  |  | 1768
|  |  | Warehouse |  |  | 1627
|  |  | Nonresidential Average |  |  | 1654
| [Capacity] | [5 empty] | Y | Btu/hr | Nominal Heating Input Capacity Boiler size (Btu/hr) for efficient unit not existing unit
| [AFUEeff] | [5 empty] | Y |  | Annual Fuel Utilization Efficiency Rating (AFUE) for Energy Efficient Equipment
| [AFUEbase] |  |  |  |  | 85% | N |  | Annual Fuel Utilization Efficiency Rating (AFUE) for Baseline Equipment
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.014346
|  |  | Grocery |  |  | 0.022412
|  |  | Health |  |  | 0.013368
|  |  | Hospital |  |  | 0.021184
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.011829
|  |  | Multifamily |  |  | 0.011829
|  |  | Office - Large |  |  | 0.010352
|  |  | Office - Small |  |  | 0.011789
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.013452
|  |  | Retail - Large |  |  | 0.014291
|  |  | Retail - Small |  |  | 0.012009
|  |  | Warehouse |  |  | 0.012093
|  |  | Nonresidential Average |  |  | 0.012386

## Boiler Tune Up
Boiler Tune Up
| Measure Code: | NR-HVC-BLRT-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
1
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = ([Capacity] * [EFLH ]*((([Effbefore] + [Ei])) / [Effbefore] – 1)) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Capacity] | [5 empty] | Y | Btu/hr | Gas Boiler input size
| [EFLH ] | Building Type | Convenience | Climate Zone | Burlington | 785 | N | Hours | Equivalent Full Load Hours for heating space
|  |  | Education |  |  | 968
|  |  | Grocery |  |  | 511
|  |  | Health |  |  | 1021
|  |  | Hospital |  |  | 906
|  |  | Industrial |  |  | 849
|  |  | Lodging |  |  | 1396
|  |  | Multifamily |  |  | 1396
|  |  | Office - Large |  |  | 1351
|  |  | Office - Small |  |  | 1290
|  |  | Religious |  |  | 1322
|  |  | Restaurant |  |  | 1036
|  |  | Retail - Large |  |  | 893
|  |  | Retail - Small |  |  | 1200
|  |  | Warehouse |  |  | 1205
|  |  | Nonresidential Average |  |  | 1197
|  |  | Convenience |  | Des Moines | 1071
|  |  | Education |  |  | 1300
|  |  | Grocery |  |  | 737
|  |  | Health |  |  | 1413
|  |  | Hospital |  |  | 1073
|  |  | Industrial |  |  | 1183
|  |  | Lodging |  |  | 1703
|  |  | Multifamily |  |  | 1703
|  |  | Office - Large |  |  | 1491
|  |  | Office - Small |  |  | 1495
|  |  | Religious |  |  | 1796
|  |  | Restaurant |  |  | 1247
|  |  | Retail - Large |  |  | 1303
|  |  | Retail - Small |  |  | 1608
|  |  | Warehouse |  |  | 1440
|  |  | Nonresidential Average |  |  | 1497
|  |  | Convenience |  | Mason City | 1224
|  |  | Education |  |  | 1497
|  |  | Grocery |  |  | 963
|  |  | Health |  |  | 1529
|  |  | Hospital |  |  | 1379
|  |  | Industrial |  |  | 1275
|  |  | Lodging |  |  | 1900
|  |  | Multifamily |  |  | 1900
|  |  | Office - Large |  |  | 1616
|  |  | Office - Small |  |  | 1673
|  |  | Religious |  |  | 1873
|  |  | Restaurant |  |  | 1381
|  |  | Retail - Large |  |  | 1394
|  |  | Retail - Small |  |  | 1768
|  |  | Warehouse |  |  | 1627
|  |  | Nonresidential Average |  |  | 1654
| [Effbefore] | [5 empty] | Y |  | Combustion Efficiency of the boiler before the tune-up
| [Ei] | [5 empty] | Y |  | Combustion Efficiency Improvement of the boiler tune-up measure
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  | 0.01631 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.013261
|  |  | Grocery |  |  | 0.021811
|  |  | Health |  |  | 0.011071
|  |  | Hospital |  |  | 0.013578
|  |  | Industrial |  |  | 0.01424
|  |  | Lodging |  |  | 0.008752
|  |  | Multifamily |  |  | 0.008752
|  |  | Office - Large |  |  | 0.010094
|  |  | Office - Small |  |  | 0.011695
|  |  | Religious |  |  | 0.011745
|  |  | Restaurant |  |  | 0.01051
|  |  | Retail - Large |  |  | 0.014243
|  |  | Retail - Small |  |  | 0.011861
|  |  | Warehouse |  |  | 0.01201
|  |  | Nonresidential Average |  |  | 0.012

## Furnace Tune Up
Furnace Tune Up
| Measure Code: | NR-HVC-FTUN-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
1
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [ΔTherms] * [Fe] * [29.3]
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = ([Capacity] * [EFLH] * ((([Effbefore] + [Ei])) / [Effbefore] – 1) ) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔTherms] | [5 empty] | C | therm | As calculated below
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh/therm | kWh per therm
| [Capacity] | [5 empty] | Y | Btu/hr | Nominal heating input capacity furnace size (Btu/hr)
| [EFLH ] | Building Type | Convenience | Climate Zone | Burlington | 785 | N | Hours | Equivalent Full Load Hours for heating space
|  |  | Education |  |  | 968
|  |  | Grocery |  |  | 511
|  |  | Health |  |  | 1021
|  |  | Hospital |  |  | 906
|  |  | Industrial |  |  | 849
|  |  | Lodging |  |  | 1396
|  |  | Multifamily |  |  | 1396
|  |  | Office - Large |  |  | 1351
|  |  | Office - Small |  |  | 1290
|  |  | Religious |  |  | 1322
|  |  | Restaurant |  |  | 1036
|  |  | Retail - Large |  |  | 893
|  |  | Retail - Small |  |  | 1200
|  |  | Warehouse |  |  | 1205
|  |  | Nonresidential Average |  |  | 1197
|  |  | Convenience |  | Des Moines | 1071
|  |  | Education |  |  | 1300
|  |  | Grocery |  |  | 737
|  |  | Health |  |  | 1413
|  |  | Hospital |  |  | 1073
|  |  | Industrial |  |  | 1183
|  |  | Lodging |  |  | 1703
|  |  | Multifamily |  |  | 1703
|  |  | Office - Large |  |  | 1491
|  |  | Office - Small |  |  | 1495
|  |  | Religious |  |  | 1796
|  |  | Restaurant |  |  | 1247
|  |  | Retail - Large |  |  | 1303
|  |  | Retail - Small |  |  | 1608
|  |  | Warehouse |  |  | 1440
|  |  | Nonresidential Average |  |  | 1497
|  |  | Convenience |  | Mason City | 1224
|  |  | Education |  |  | 1497
|  |  | Grocery |  |  | 963
|  |  | Health |  |  | 1529
|  |  | Hospital |  |  | 1379
|  |  | Industrial |  |  | 1275
|  |  | Lodging |  |  | 1900
|  |  | Multifamily |  |  | 1900
|  |  | Office - Large |  |  | 1616
|  |  | Office - Small |  |  | 1673
|  |  | Religious |  |  | 1873
|  |  | Restaurant |  |  | 1381
|  |  | Retail - Large |  |  | 1394
|  |  | Retail - Small |  |  | 1768
|  |  | Warehouse |  |  | 1627
|  |  | Nonresidential Average |  |  | 1654
| [Effbefore] | [5 empty] | Y |  | Combustion Efficiency of the boiler before the tune-up
| [Ei] | [5 empty] | Y |  | Combustion Efficiency Improvement of the boiler tune-up measure
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.014346
|  |  | Grocery |  |  | 0.022412
|  |  | Health |  |  | 0.013368
|  |  | Hospital |  |  | 0.021184
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.011829
|  |  | Multifamily |  |  | 0.011829
|  |  | Office - Large |  |  | 0.010352
|  |  | Office - Small |  |  | 0.011789
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.013452
|  |  | Retail - Large |  |  | 0.014291
|  |  | Retail - Small |  |  | 0.012009
|  |  | Warehouse |  |  | 0.012093
|  |  | Nonresidential Average |  |  | 0.012386

## Geothermal Source Heat Pump
Geothermal Source Heat Pump
| Measure Code: | NR-HVAC-GSHP-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Cost Known | Actual minus $1936 per ton of capacity
|  | Cost Unknown | $3957 per ton minus $1936 per ton of capacity
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [([EFLH_Cool] * [Capacity_Cool] * ([PLF_Cool] * (1 / [EER_Base] – 1 / [EEREE-PL] )+ [FLF_Cool] * (1 / [EER_Base] – 1 / [EEREE-FL] ))) / [1000]] + [([EFLH_Heat] * [Capacity_Heat] * ([PLF_Heat] * (1 / [HSPF_Base] – 1 / (([COPEE- PL] * [3.412]) )) + [FLF_Heat] * (1 / [HSPF_Base] – 1 / (([COPEE- FL] * [3.412]) )))) / [1000]]
| Time of Sale Demand (ΔkW) | = (([Capacity_Cool] * (1 / [EER_base] - 1 / [EEREE-FL] )) / [1000]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [EEREE - PL] | System type | Closed loop | = 0.0000315 * [EER]^3 - 0.0111 * [EER]^2 + 0.959*[EER]
|  |  | Open loop | = 0.00005 * [EER]^3 - 0.0145 * [EER]^2 + 0.93 * [EER]
| [EEREE - FL] | System type | Closed loop | = 0.0000315 * [EER]^3 - 0.0111 * [EER]^2 + 0.959*[EER]
|  |  | Open loop | = 0.00005 * [EER]^3 - 0.0145 * [EER]^2 + 0.93 * [EER]
| [COPEE - PL] | System type | Closed loop | = 0.000416 * [COP]^3 - 0.041 * [COP]^2 + 1.0086 * [COP]
|  |  | Open loop | = 0.00067 * [COP]^3 - 0.0531 * [COP]^2 + 0.976 * [COP]
| [COPEE - FL] | System type | Closed loop | = 0.000416 * [COP]^3 - 0.041 * [COP]^2 + 1.0086 * [COP]
|  |  | Open loop | = 0.00067 * [COP]^3 - 0.0531 * [COP]^2 + 0.976 * [COP]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLHCool] | Building Type | Convenience | Climate Zone | Burlington | 1477 | N | Hours | Equivalent Full Load Hours for cooling
|  |  | Education |  |  | 1059
|  |  | Grocery |  |  | 1975
|  |  | Health |  |  | 1169
|  |  | Hospital |  |  | 1843
|  |  | Industrial |  |  | 1185
|  |  | Lodging |  |  | 1503
|  |  | Multifamily |  |  | 1503
|  |  | Office - Large |  |  | 1227
|  |  | Office - Small |  |  | 1094
|  |  | Religious |  |  | 1109
|  |  | Restaurant |  |  | 1325
|  |  | Retail - Large |  |  | 1209
|  |  | Retail - Small |  |  | 1179
|  |  | Warehouse |  |  | 954
|  |  | Nonresidential Average |  |  | 1087
|  |  | Convenience |  | Des Moines | 1351
|  |  | Education |  |  | 937
|  |  | Grocery |  |  | 1735
|  |  | Health |  |  | 1064
|  |  | Hospital |  |  | 1673
|  |  | Industrial |  |  | 1063
|  |  | Lodging |  |  | 1355
|  |  | Multifamily |  |  | 1355
|  |  | Office - Large |  |  | 1143
|  |  | Office - Small |  |  | 981
|  |  | Religious |  |  | 1031
|  |  | Restaurant |  |  | 1176
|  |  | Retail - Large |  |  | 1078
|  |  | Retail - Small |  |  | 1039
|  |  | Warehouse |  |  | 866
|  |  | Nonresidential Average |  |  | 979
|  |  | Convenience |  | Mason City | 1128
|  |  | Education |  |  | 712
|  |  | Grocery |  |  | 1483
|  |  | Health |  |  | 896
|  |  | Hospital |  |  | 1363
|  |  | Industrial |  |  | 856
|  |  | Lodging |  |  | 1084
|  |  | Multifamily |  |  | 1084
|  |  | Office - Large |  |  | 972
|  |  | Office - Small |  |  | 787
|  |  | Religious |  |  | 797
|  |  | Restaurant |  |  | 956
|  |  | Retail - Large |  |  | 861
|  |  | Retail - Small |  |  | 843
|  |  | Warehouse |  |  | 694
|  |  | Nonresidential Average |  |  | 779
| [CapacityCool] | [5 empty] | Y | Btu/hr | Cooling Capacity for Geothermal Source Heat Pump, 1 ton = 12000 Btu/hr
| [PLFCool] | Speed | Variable |  |  | 0.85 | N |  | Part load cooling mode operation
|  |  | Single/Constant |  |  | 0
| [FLFCool ] | Speed | Variable |  |  | 0.15 | N |  | Full load cooling mode operation factor
|  |  | Single/Constant |  |  | 1
| [EERBase] |  |  |  |  | 11.8 | N |  | SEER Efficiency of new baseline AHSP unit
| [EEREE - PL] | [5 empty] | C |  | Full Load EER Efficiency of ENERGY STAR GSHP unit
| [EFLHHeat] | Building Type | Convenience | Climate Zone | Burlington | 785 | N | Hours | Equivalent Full Load Hours for heating space
|  |  | Education |  |  | 968
|  |  | Grocery |  |  | 511
|  |  | Health |  |  | 1021
|  |  | Hospital |  |  | 906
|  |  | Industrial |  |  | 849
|  |  | Lodging |  |  | 1396
|  |  | Multifamily |  |  | 1396
|  |  | Office - Large |  |  | 1351
|  |  | Office - Small |  |  | 1290
|  |  | Religious |  |  | 1322
|  |  | Restaurant |  |  | 1036
|  |  | Retail - Large |  |  | 893
|  |  | Retail - Small |  |  | 1200
|  |  | Warehouse |  |  | 1205
|  |  | Nonresidential Average |  |  | 1197
|  |  | Convenience |  | Des Moines | 1071
|  |  | Education |  |  | 1300
|  |  | Grocery |  |  | 737
|  |  | Health |  |  | 1413
|  |  | Hospital |  |  | 1073
|  |  | Industrial |  |  | 1183
|  |  | Lodging |  |  | 1703
|  |  | Multifamily |  |  | 1703
|  |  | Office - Large |  |  | 1491
|  |  | Office - Small |  |  | 1495
|  |  | Religious |  |  | 1796
|  |  | Restaurant |  |  | 1247
|  |  | Retail - Large |  |  | 1303
|  |  | Retail - Small |  |  | 1608
|  |  | Warehouse |  |  | 1440
|  |  | Nonresidential Average |  |  | 1497
|  |  | Convenience |  | Mason City | 1224
|  |  | Education |  |  | 1497
|  |  | Grocery |  |  | 963
|  |  | Health |  |  | 1529
|  |  | Hospital |  |  | 1379
|  |  | Industrial |  |  | 1275
|  |  | Lodging |  |  | 1900
|  |  | Multifamily |  |  | 1900
|  |  | Office - Large |  |  | 1616
|  |  | Office - Small |  |  | 1673
|  |  | Religious |  |  | 1873
|  |  | Restaurant |  |  | 1381
|  |  | Retail - Large |  |  | 1394
|  |  | Retail - Small |  |  | 1768
|  |  | Warehouse |  |  | 1627
|  |  | Nonresidential Average |  |  | 1654
| [CapacityHeat] | [5 empty] | Y | Btu/hr | Full Load Heating Capacity of Geothermal Source Heat Pump (1 ton = 12,000 Btu/hr)
| [PLFHeat] | Speed | Variable |  |  | 0.5 | N |  | Part load heating mode operation
|  |  | Single/Constant |  |  | 0
| [FLFHeat] | Speed | Variable |  |  | 0.5 | N |  | Full load heating mode operation
|  |  | Single/Constant |  |  | 1
| [HSPFBase] |  |  |  |  | 8.2 | N | kBtu/kWh | Heating System Performance Factor of new replacement baseline heating system
| [COPEE - PL ] | [5 empty] | C |  | Part Load Coeffcient of Performance of efficient unit
| [3.412] |  |  |  |  | 3.412 | N |  | Constant to ocnvert the COP of the unit to the Heating Season Performance Factor (HSPF)
| [EERbase] |  |  |  |  | 11.8 | N |  | EER Efficiency of new baseline unit
| [EEREE - FL] | [5 empty] | C |  | Full Load EER Efficiency of ENERGY STAR GSHP unit
| [COPEE - FL ] | [5 empty] | C |  | Full Load Coeffcient of Performance of efficient unit
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling
|  |  | Education |  |  | 61.9%
|  |  | Grocery |  |  | 90.6%
|  |  | Health |  |  | 88.2%
|  |  | Hospital |  |  | 95%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 88.8%
|  |  | Multifamily |  |  | 88.8%
|  |  | Office - Large |  |  | 74.2%
|  |  | Office - Small |  |  | 70.9%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 91.5%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 87.7%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 79.8%

## Sm. Commercial Prog. Thermostat
Sm. Commercial Prog. Thermostat
| Measure Code: | NR-HVC-PROG-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
4
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Labor cost of implementation | Known | Actual
|  | Unknown | 181
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWh_cooling] + [∆kWh_heating]
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = ([Sqft] * [Savings Factor_heat])/(100 * [EfficiencyRating(exist)_heat])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ([Sqft] * [Savings Factor_cool]) / [EfficiencyRating(exist)_cool]
| [∆kWh_heating] |  |  | = ([Sqft] * [Savings Factor_heat]) / ([3.412] * [EfficiencyRating(exist)_electric heat])
| [∆kWh_heating] |  |  | = [ΔTherms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Sqft] | [5 empty] | Y | ft2 | Square footage of building controlled by thermostat
| [EfficiencyRating(exist)_cool] | [5 empty] | Y | btuhr/w | Efficiency rating of existing cooling equipment EER (btu hr/w)
| [Savings Factor_cool] |  |  |  |  | 0.53 | N | kBtu/sf-yr | Savings factor for cooling
| [Savings Factor_heat] |  |  |  |  | 0.85 | N | kBtu/sf-yr | Savings factor for heating
| [3.412] |  |  |  |  | 3.412 | N |  | Conversion from kBtu to kWh
| [EfficiencyRating(exist)_electric heat] | [5 empty] | Y |  | Efficiency rating of existing heating equipment EER (AFUE)
| [ΔTherms] | [5 empty] | C | therm | Therm impact
| [Fe] |  |  |  |  | 3.14% | N |  | Percentage of heating energy consumed by fans
| [29.3] |  |  |  |  | 29.3 | N |  | Conversion from therms to kWh
| [EfficiencyRating(exist)_heat] | [5 empty] | Y |  | Efficiency rating of existing heating equipment (AFUE)
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.014346
|  |  | Grocery |  |  | 0.022412
|  |  | Health |  |  | 0.013368
|  |  | Hospital |  |  | 0.021184
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.011829
|  |  | Multifamily |  |  | 0.011829
|  |  | Office - Large |  |  | 0.010352
|  |  | Office - Small |  |  | 0.011789
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.013452
|  |  | Retail - Large |  |  | 0.014291
|  |  | Retail - Small |  |  | 0.012009
|  |  | Warehouse |  |  | 0.012093
|  |  | Nonresidential Average |  |  | 0.012386

## VFDs for HVAC Pumps
VFDs for HVAC Pumps
| Measure Code: | NR-HVC-VFHP-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  | Actual
|  | Unknown | Horse Power | 1-9 | 1874
|  |  |  | 10-19 | 2967
|  |  |  | 20-29 | 4060
|  |  |  | 30-39 | 5154
|  |  |  | 40-49 | 6247
|  |  |  | 50-59 | 7340
|  |  |  | 60-69 | 8433
|  |  |  | 70-75 | 9526
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([BHP] ) / [EFFi] * [Hours] * [ESF]
| Time of Sale Demand (ΔkW) | =[BHP] / [EFFi] * [DSF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [BHP] |  |  | = ([Nominal motor HP] * [Motor load factor])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [BHP] | [5 empty] | C |  | System Brake Horsepower
| [Nominal motor HP] | [5 empty] | Y |  | Nominal motor horse power
| [Motor load factor] |  |  |  |  | 65% | Y |  | Motor load factor
| [EFFi] | [5 empty] | Y |  | Motor efficiency, installed
| [Hours] | Building Type | Convenience | Pump Type | Hot Water | 3628 | Y | Hours | Default hours are provided for HVAC applications which vary by building type
|  |  | Education |  |  | 3566
|  |  | Grocery |  |  | 2551
|  |  | Health |  |  | 3957
|  |  | Hospital |  |  | 4260
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 5287
|  |  | Multifamily |  |  | 5287
|  |  | Office - Large |  |  | 5864
|  |  | Office - Small |  |  | 4482
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 4127
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 3985
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 4253
|  |  | Convenience |  | Chilled Water | 2690
|  |  | Education |  |  | 2833
|  |  | Grocery |  |  | 3994
|  |  | Health |  |  | 4369
|  |  | Hospital |  |  | 4647
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5292
|  |  | Multifamily |  |  | 5292
|  |  | Office - Large |  |  | 4608
|  |  | Office - Small |  |  | 2702
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 2974
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 2120
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 2331
| [ESF] | Application | Hot Water Centrifugal Pump |  |  | 0.424 | N | kW/HP | Energy savings factor varies by VFD application
|  |  | Chilled Water Centrifugal Pump |  |  | 0.411
| [DSF] | Application | Hot Water Centrifugal Pump |  |  | 0 | N | kW/HP | Demand Savings Factor varies by VFD application. Units are kW/HP. Values listed below are based on typical peak load for the listed application
|  |  | Chilled Water Centrifugal Pump |  |  | 0.299

## VFDs for HVAC Sup. and Ret. Fan
VFDs for HVAC Sup. and Ret. Fan
| Measure Code: | NR-HVC-VFDF-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  | Actual
|  | Unknown | Horse Power | 1-9 | 1874
|  |  |  | 10-19 | 2967
|  |  |  | 20-29 | 4060
|  |  |  | 30-39 | 5154
|  |  |  | 40-49 | 6247
|  |  |  | 50-59 | 7340
|  |  |  | 60-69 | 8433
|  |  |  | 70-75 | 9526
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([kWh_Base]-[kWh_Retrofit]) *(1+[IE_energy])
| Time of Sale Demand (ΔkW) | =([kW_Base]-[kW_Retrofit]) *(1+[IE_demand])
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh_Base] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[RHRS_Base]*[∑(%FF*PLR_Base)]
| [kWh_Retrofit] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[RHRS_Base]*[∑(%FF*PLR_Retrofit)]
| [kW_Base] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[PLR_BaseFFPeak]
| [kW_Retrofit] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[PLR_RetrofitFFPeak]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWh_Base] | [5 empty] | C |  | Baseline annual energy consumption
| [kWh_Retrofit] | [5 empty] | C |  | Retrofit annual energy consumption
| [0.746] |  |  |  |  | 0.746 | N |  | Conversion factor for HP to kWh
| [HP] | [5 empty] | Y | HP | Nominal horsepower of controlled motor
| [LF] |  |  |  |  | 0.65 | Y | Percentage | Load Factor; Motor Load at Fan Design CFM
| [η_motor] | [5 empty] | Y | Percentage | Installed nominal/nameplate motor efficiency
| [RHRS_Base] | Building Type | Convenience |  |  | 4630 | Y | Hours | Annual operating hours for fan motor based on building type
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
| [∑(%FF*PLR_Base)] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | Sum of %FF * Part Load Ratio based on baseline flow control type
|  |  | Discharge Dampers |  |  | 0.8
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 0.78
|  |  | Inlet Damper Box |  |  | 0.69
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.63
|  |  | Inlet Vane Dampers |  |  | 0.53
|  |  | Outlet Damper, FC Fans |  |  | 0.53
|  |  | Eddy Current Drives |  |  | 0.49
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.39
|  |  | VFD with duct static pressure controls |  |  | 0.3
|  |  | VFD with low/no duct static pressure |  |  | 0.27
| [∑(%FF*PLR_Retrofit)] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | Sum of %FF * Part Load Ratio based on retrofit flow control type
|  |  | Discharge Dampers |  |  | 0.8
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 0.78
|  |  | Inlet Damper Box |  |  | 0.69
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.63
|  |  | Inlet Vane Dampers |  |  | 0.53
|  |  | Outlet Damper, FC Fans |  |  | 0.53
|  |  | Eddy Current Drives |  |  | 0.49
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.39
|  |  | VFD with duct static pressure controls |  |  | 0.3
|  |  | VFD with low/no duct static pressure |  |  | 0.27
| [IE_energy] |  |  |  |  | 0.157 | N |  | HVAC interactive effects factor for energy
| [kW_Base] | [5 empty] | C | kW | Baseline summer coincident peak demand
| [kW_Retrofit] | [5 empty] | C | kW | Retrofit summer coincident peak demand
| [PLR_BaseFFPeak] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)
|  |  | Discharge Dampers |  |  | 0.97
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 1.02
|  |  | Inlet Damper Box |  |  | 0.92
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.85
|  |  | Inlet Vane Dampers |  |  | 0.83
|  |  | Outlet Damper, FC Fans |  |  | 0.91
|  |  | Eddy Current Drives |  |  | 0.9
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.81
|  |  | VFD with duct static pressure controls |  |  | 0.76
|  |  | VFD with low/no duct static pressure |  |  | 0.75
| [PLR_RetrofitFFPeak] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the retrofit flow control type (default average flow fraction during peak period = 90%)
|  |  | Discharge Dampers |  |  | 0.97
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 1.02
|  |  | Inlet Damper Box |  |  | 0.92
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.85
|  |  | Inlet Vane Dampers |  |  | 0.83
|  |  | Outlet Damper, FC Fans |  |  | 0.91
|  |  | Eddy Current Drives |  |  | 0.9
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.81
|  |  | VFD with duct static pressure controls |  |  | 0.76
|  |  | VFD with low/no duct static pressure |  |  | 0.75
| [IE_demand] |  |  |  |  | 0.157 | N |  | HVAC interactive effects factor for summer coincident peak demand

## CFL - Standard
CFL - Standard
| Measure Code: | NR-LTG-STCFL-V02-180101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Convenience | 2.1598
|  | Education | 3
|  | Grocery | 2.1445
|  | Health | 2.6274
|  | Hospital | 1.5337
|  | Industrial | 3
|  | Lodging | 3
|  | Multifamily | 3
|  | Office - Large | 3
|  | Office - Small | 3
|  | Religious | 3
|  | Restaurant | 1.8372
|  | Retail - Large | 2.46
|  | Retail - Small | 2.7071
|  | Warehouse | 3
|  | Nonresidential Average | 3
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Type | Retail TOS | Lumens | < 2000 lumens | 1.03
|  |  |  | > 2000 lumens | 2.76
|  | Direct Install |  | < 2000 lumens | 13.2
|  |  |  | ≥ 2000 lumens | 16.2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
| Building Type | Convenience | 0.91 | $2.17 for bulbs <2,000 lumens $3.44 for bulbs ≥2,000 lumens
|  | Education | 2.24
|  | Grocery | 0.9
|  | Health | 1.1
|  | Hospital | 0.64
|  | Industrial | 1.47
|  | Lodging | 1.37
|  | Multifamily | 1.37
|  | Office - Large | 1.44
|  | Office - Small | 1.44
|  | Religious | 1.74
|  | Restaurant | 0.77
|  | Retail - Large | 1.03
|  | Retail - Small | 1.14
|  | Warehouse | 1.44
|  | Nonresidential Average | 1.37
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ ISR] * [Hours] *(- [IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lumen Range | 250-309 |  |  | 19 | Y | Watts | Actual (if retrofit) or based on lumens of CFL bulb installed
|  |  | 310-749 |  |  | 23
|  |  | 750-1049 |  |  | 33.9
|  |  | 1050-1489 |  |  | 42.5
|  |  | 1490-2600 |  |  | 57.5
|  |  | 2601-3000 |  |  | 117.4
|  |  | 3001-3999 |  |  | 156.2
|  |  | 4000-6000 |  |  | 230.1
| [WattsEE] | Lumen Range | 250-309 |  |  | 5.1 | Y | Watts | Actual wattage of CFL purchased or installed
|  |  | 310-749 |  |  | 9.4
|  |  | 750-1049 |  |  | 13.4
|  |  | 1050-1489 |  |  | 18.9
|  |  | 1490-2600 |  |  | 24.8
|  |  | 2601-3000 |  |  | 41.1
|  |  | 3001-3999 |  |  | 53.8
|  |  | 4000-6000 |  |  | 65
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Education |  |  | 1.15
|  |  | Grocery |  |  | 1.14
|  |  | Health |  |  | 0.058
|  |  | Hospital |  |  | 1.24
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 0.84
|  |  | Multifamily |  |  | 0.84
|  |  | Office - Large |  |  | 1.13
|  |  | Office - Small |  |  | 1.15
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1.16
|  |  | Retail - Large |  |  | 1.14
|  |  | Retail - Small |  |  | 1.12
|  |  | Warehouse |  |  | 1.09
|  |  | Nonresidential Average |  |  | 1.13
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] | Program | Retail (Time of Sale) |  |  | 95% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit |  |  | 97%
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.43
|  |  | Grocery |  |  | 0.32
|  |  | Health |  |  | 1.1
|  |  | Hospital |  |  | 0.52
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.57
|  |  | Multifamily |  |  | 0.57
|  |  | Office - Large |  |  | 0.6
|  |  | Office - Small |  |  | 0.4
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0.44
|  |  | Retail - Large |  |  | 0.43
|  |  | Retail - Small |  |  | 0.46
|  |  | Warehouse |  |  | 0.44
|  |  | Nonresidential Average |  |  | 0.43
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.14
|  |  | Health |  |  | 0.48
|  |  | Hospital |  |  | 0.22
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.25
|  |  | Multifamily |  |  | 0.25
|  |  | Office - Large |  |  | 0.26
|  |  | Office - Small |  |  | 0.17
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0.19
|  |  | Retail - Large |  |  | 0.19
|  |  | Retail - Small |  |  | 0.2
|  |  | Warehouse |  |  | 0.19
|  |  | Nonresidential Average |  |  | 0.19
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.67
|  |  | Grocery |  |  | 1.22
|  |  | Health |  |  | 1.55
|  |  | Hospital |  |  | 1.53
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.15
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.24
|  |  | Office - Small |  |  | 1.45
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.39
|  |  | Retail - Large |  |  | 1.34
|  |  | Retail - Small |  |  | 1.39
|  |  | Warehouse |  |  | 1.43
|  |  | Nonresidential Average |  |  | 1.42
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 10% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 62.3%
|  |  | Grocery |  |  | 10%
|  |  | Health |  |  | 96.1%
|  |  | Hospital |  |  | 10%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 19.8%
|  |  | Multifamily |  |  | 19.8%
|  |  | Office - Large |  |  | 48.4%
|  |  | Office - Small |  |  | 63.6%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 96.7%
|  |  | Retail - Large |  |  | 10%
|  |  | Retail - Small |  |  | 10%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 71.7%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.018
|  |  | Grocery |  |  | 0.014
|  |  | Health |  |  | 0.047
|  |  | Hospital |  |  | 0.022
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.024
|  |  | Multifamily |  |  | 0.024
|  |  | Office - Large |  |  | 0.026
|  |  | Office - Small |  |  | 0.017
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0.019
|  |  | Retail - Large |  |  | 0.018
|  |  | Retail - Small |  |  | 0.019
|  |  | Warehouse |  |  | 0.019
|  |  | Nonresidential Average |  |  | 0.018
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## CFL - Specialty
CFL - Specialty
| Measure Code: | NR-LTG-SPCFL-V02-180101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Convenience | 2.1598
|  | Education | 5.3277
|  | Grocery | 2.1445
|  | Health | 2.6274
|  | Hospital | 1.5337
|  | Industrial | 3.5088
|  | Lodging | 3.2669
|  | Multifamily | 3.2669
|  | Office - Large | 3.4247
|  | Office - Small | 3.4247
|  | Religious | 4.1459
|  | Restaurant | 1.8372
|  | Retail - Large | 2.46
|  | Retail - Small | 2.7071
|  | Warehouse | 3.4247
|  | Nonresidential Average | 3.2626
| Measure Cost: | [8 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Direct Install) |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Bulb Type | Directional | CFL Wattage | < 20W | 0.56 | 17.84
|  |  |  | ≥20W | -1.25 | 19.31
|  | Decorative and Globes |  | <15W | 3.08 | 17.8
|  |  |  | ≥15W | 2.61 | 18.15
|  | Other / Unknown |  |  | 1.81 | 17.82
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable 2 Input | Dependent Variable 2 Options | Life of Component | Cost
| Building Type | Convenience | Bulb Type | Directional | 0.93 | $7.28 for < 20W, $10.56 for ≥20W
|  | Education |  |  | 2.29
|  | Grocery |  |  | 0.92
|  | Health |  |  | 1.13
|  | Hospital |  |  | 0.66
|  | Industrial |  |  | 1.51
|  | Lodging |  |  | 1.4
|  | Multifamily |  |  | 1.4
|  | Office - Large |  |  | 1.47
|  | Office - Small |  |  | 1.47
|  | Religious |  |  | 1.78
|  | Restaurant |  |  | 0.79
|  | Retail - Large |  |  | 1.06
|  | Retail - Small |  |  | 1.16
|  | Warehouse |  |  | 1.47
|  | Nonresidential Average |  |  | 1.4
|  | Convenience |  | Decorative/Globe | 0.71 | $4.73 for <15W, $5.54 for ≥15W
|  | Education |  |  | 1.76
|  | Grocery |  |  | 0.71
|  | Health |  |  | 0.87
|  | Hospital |  |  | 0.51
|  | Industrial |  |  | 1.16
|  | Lodging |  |  | 1.08
|  | Multifamily |  |  | 1.08
|  | Office - Large |  |  | 1.13
|  | Office - Small |  |  | 1.13
|  | Religious |  |  | 1.37
|  | Restaurant |  |  | 0.61
|  | Retail - Large |  |  | 0.81
|  | Retail - Small |  |  | 0.89
|  | Warehouse |  |  | 1.13
|  | Nonresidential Average |  |  | 1.08
|  | Convenience |  | Unknown | 0.82 | 6.01
|  | Education |  |  | 2.02
|  | Grocery |  |  | 0.81
|  | Health |  |  | 1
|  | Hospital |  |  | 0.58
|  | Industrial |  |  | 1.33
|  | Lodging |  |  | 1.24
|  | Multifamily |  |  | 1.24
|  | Office - Large |  |  | 1.3
|  | Office - Small |  |  | 1.3
|  | Religious |  |  | 1.58
|  | Restaurant |  |  | 0.7
|  | Retail - Large |  |  | 0.93
|  | Retail - Small |  |  | 1.03
|  | Warehouse |  |  | 1.3
|  | Nonresidential Average |  |  | 1.24
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]
| Time of Sale Demand (ΔkW) | =([WattsBase[ - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (- [IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Bulb Type (EISA Exempt) | 3-way | Lumen range | 250-449 | 21.3 | N | Watts | Based on lumens of CFL bulb installed and includes blend of incandescent/halogen , CFL and LED by weightings provided in table below . Note that when an IA net-to-gross (NTG) factor is determined for this measure, this blended baseline should be replaced with the Incandescent/Halogen baseline only.
[5 empty] | 450-799 | 34.3
[5 empty] | 800-1099 | 50.3
[5 empty] | 1100-1599 | 63.4
[5 empty] | 1600-1999 | 84.5
[5 empty] | 2000-2549 | 106.7
[5 empty] | 2550-2999 | 128.3
|  |  | Globe (medium and intermediate bases less than 750 lumens) |  | 90-179 | 8.6
[5 empty] | 180-249 | 13
[5 empty] | 250-349 | 21.1
[5 empty] | 350-749 | 33.6
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 70-89 | 8.4
[5 empty] | 90-149 | 12.5
[5 empty] | 150-299 | 20.9
[5 empty] | 300-749 | 33.3
|  |  | Globe (candelabra bases less than 1050 lumens) |  | 90-179 | 8.6
[5 empty] | 180-249 | 13
[5 empty] | 250-349 | 21.1
[5 empty] | 350-499 | 33.4
[5 empty] | 500-1049 | 50.2
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra bases less than 1050 lumens) |  | 70-89 | 8.4
[5 empty] | 90-149 | 12.5
[5 empty] | 150-299 | 20.8
[5 empty] | 300-499 | 33.2
[5 empty] | 500-1049 | 50.2
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) |  | 420-472 | 33.9
[5 empty] | 473-524 | 38
[5 empty] | 525-714 | 42.4
[5 empty] | 715-937 | 54.8
[5 empty] | 938-1259 | 63.7
[5 empty] | 1260-1399 | 76.1
[5 empty] | 1400-1739 | 85.1
[5 empty] | 1740-2174 | 102.5
[5 empty] | 2175-2624 | 127.7
[5 empty] | 2625-2999 | 151.2
[5 empty] | 3000-4500 | 175
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" |  | 400-449 | 33.7
[5 empty] | 450-499 | 37.9
[5 empty] | 500-649 | 42.2
[5 empty] | 650-1199 | 55.2
|  |  | *ER30, BR30, BR40, or ER40 |  | 400-449 | 34.1
[5 empty] | 450-499 | 38.4
[5 empty] | 500-649 | 42.6
|  |  | BR30, BR40, or ER40 |  | 650-1419 | 55
|  |  | R20 |  | 400-449 | 34.1
[5 empty] | 450-719 | 38
|  |  | *All reflector lamps below lumen ranges specified above |  | 200-299 | 17
[5 empty] | 300-399 | 25.5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) |  | 250-309 | 20.9
[5 empty] | 310-749 | 24.8
[5 empty] | 750-1049 | 36.8
[5 empty] | 1050-1489 | 45.6
[5 empty] | 1490-2600 | 61.8
| [WattsEE] | Bulb Type (EISA Exempt) | 3-way | Lumen range | 250-449 | 6.4 | Y | Watts | Actual wattage of energy efficient specialty bulb purchased, if unknown, assume the following defaults
[5 empty] | 450-799 | 11.4
[5 empty] | 800-1099 | 13
[5 empty] | 1100-1599 | 20.8
[5 empty] | 1600-1999 | 26
[5 empty] | 2000-2549 | 32.2
[5 empty] | 2550-2999 | 40
|  |  | Globe (medium and intermediate bases less than 750 lumens) |  | 90-179 | 3
[5 empty] | 180-249 | 4.8
[5 empty] | 250-349 | 6.7
[5 empty] | 350-749 | 9.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 70-89 | 1.8
[5 empty] | 90-149 | 2.7
[5 empty] | 150-299 | 5
[5 empty] | 300-749 | 7.5
|  |  | Globe (candelabra bases less than 750 lumens) |  | 90-179 | 3
[5 empty] | 180-249 | 4.8
[5 empty] | 250-349 | 6.7
[5 empty] | 350-499 | 9.4
[5 empty] | 500-1049 | 15.5
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) |  | 70-89 | 1.8
[5 empty] | 90-149 | 2.7
[5 empty] | 150-299 | 5
[5 empty] | 300-499 | 7.7
[5 empty] | 500-1049 | 15.5
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) |  | 420-472 | 11
[5 empty] | 473-524 | 12.5
[5 empty] | 525-714 | 14.9
[5 empty] | 715-937 | 15.6
[5 empty] | 938-1259 | 21.1
[5 empty] | 1260-1399 | 23
[5 empty] | 1400-1739 | 31.4
[5 empty] | 1740-2174 | 39.1
[5 empty] | 2175-2624 | 48
[5 empty] | 2625-2999 | 56.2
[5 empty] | 3000-4500 | 75
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" |  | 400-449 | 10.6
[5 empty] | 450-499 | 11.9
[5 empty] | 500-649 | 14.4
[5 empty] | 650-1199 | 18.5
|  |  | *ER30, BR30, BR40, or ER40 |  | 400-449 | 10.6
[5 empty] | 450-499 | 11.9
[5 empty] | 500-649 | 14.4
|  |  | BR30, BR40, or ER 40 |  | 650-1419 | 18
|  |  | R20 |  | 400-449 | 10.6
[5 empty] | 450-719 | 12.5
|  |  | *All reflector lamps below lumen ranges specified above |  | 200-299 | 6.2
[5 empty] | 300-399 | 8.7
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) |  | 250-309 | 5.1
[5 empty] | 310-749 | 9.5
[5 empty] | 750-1049 | 13.5
[5 empty] | 1050-1489 | 18.9
[5 empty] | 1490-2600 | 24.8
| [ISR] | Program | Retail (Time of Sale) |  |  | 95% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit |  |  | 97%
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Education |  |  | 1.15
|  |  | Grocery |  |  | 1.14
|  |  | Health |  |  | 0.058
|  |  | Hospital |  |  | 1.24
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 0.84
|  |  | Multifamily |  |  | 0.84
|  |  | Office - Large |  |  | 1.13
|  |  | Office - Small |  |  | 1.15
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1.16
|  |  | Retail - Large |  |  | 1.14
|  |  | Retail - Small |  |  | 1.12
|  |  | Warehouse |  |  | 1.09
|  |  | Nonresidential Average |  |  | 1.13
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.43
|  |  | Grocery |  |  | 0.32
|  |  | Health |  |  | 1.1
|  |  | Hospital |  |  | 0.52
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.57
|  |  | Multifamily |  |  | 0.57
|  |  | Office - Large |  |  | 0.6
|  |  | Office - Small |  |  | 0.4
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0.44
|  |  | Retail - Large |  |  | 0.43
|  |  | Retail - Small |  |  | 0.46
|  |  | Warehouse |  |  | 0.44
|  |  | Nonresidential Average |  |  | 0.43
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.14
|  |  | Health |  |  | 0.48
|  |  | Hospital |  |  | 0.22
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.25
|  |  | Multifamily |  |  | 0.25
|  |  | Office - Large |  |  | 0.26
|  |  | Office - Small |  |  | 0.17
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0.19
|  |  | Retail - Large |  |  | 0.19
|  |  | Retail - Small |  |  | 0.2
|  |  | Warehouse |  |  | 0.19
|  |  | Nonresidential Average |  |  | 0.19
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.67
|  |  | Grocery |  |  | 1.22
|  |  | Health |  |  | 1.55
|  |  | Hospital |  |  | 1.53
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.15
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.24
|  |  | Office - Small |  |  | 1.45
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.39
|  |  | Retail - Large |  |  | 1.34
|  |  | Retail - Small |  |  | 1.39
|  |  | Warehouse |  |  | 1.43
|  |  | Nonresidential Average |  |  | 1.42
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 10% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 62.3%
|  |  | Grocery |  |  | 10%
|  |  | Health |  |  | 96.1%
|  |  | Hospital |  |  | 10%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 19.8%
|  |  | Multifamily |  |  | 19.8%
|  |  | Office - Large |  |  | 48.4%
|  |  | Office - Small |  |  | 63.6%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 96.7%
|  |  | Retail - Large |  |  | 10%
|  |  | Retail - Small |  |  | 10%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 71.7%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.018
|  |  | Grocery |  |  | 0.014
|  |  | Health |  |  | 0.047
|  |  | Hospital |  |  | 0.022
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.024
|  |  | Multifamily |  |  | 0.024
|  |  | Office - Large |  |  | 0.026
|  |  | Office - Small |  |  | 0.017
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0.019
|  |  | Retail - Large |  |  | 0.018
|  |  | Retail - Small |  |  | 0.019
|  |  | Warehouse |  |  | 0.019
|  |  | Nonresidential Average |  |  | 0.018
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## LED Lamp - Standard
LED Lamp - Standard
| Measure Code: | NR-LTG-LEDA-V03-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Agricultural Animal Housing and Warehousing | 7.2887
|  | Convenience | 4.5968
|  | Education | 11.3388
|  | Exterior Lighting | 4.5515
|  | Grocery | 4.5642
|  | Health | 5.592
|  | Hospital | 3.2643
|  | Industrial | 7.4677
|  | Lodging | 6.953
|  | Multifamily | 6.953
|  | Office - Large | 7.2887
|  | Office - Small | 7.2887
|  | Religious | 8.8238
|  | Restaurant | 3.9102
|  | Retail - Large | 5.2357
|  | Retail - Small | 5.7615
|  | Warehouse | 7.2887
|  | Nonresidential Average | 6.9439
|  | Unconditioned building | As specific building above
|  | Refrigerated Cases | As specific building above
|  | Freezer Cases | As specific building above
| Measure Cost: | [9 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Incremental Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  |  |  | Actual
|  | Unknown | CRI | <90 | Product Type | ENERGY STAR | 1.19
[6 empty] | CEE Tier 2 | 1.32
|  |  |  | >=90 |  | ENERGY STAR | 1.51
[6 empty] | CEE Tier 2 | 1.58
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Life of Component | Cost
| Lumen Range | <310 and >3300 | Installation Location | Agricultural Animal Housing and Warehousing |  |  |  |  | 2.8887 | 1.97
|  |  |  | Convenience |  |  |  |  | 1.8
|  |  |  | Education |  |  |  |  | 4.5
|  |  |  | Exterior Lighting |  |  |  |  | 1.8039
|  |  |  | Grocery |  |  |  |  | 1.8
|  |  |  | Health |  |  |  |  | 2.2
|  |  |  | Hospital |  |  |  |  | 1.3
|  |  |  | Industrial |  |  |  |  | 3
|  |  |  | Lodging |  |  |  |  | 2.8
|  |  |  | Multifamily |  |  |  |  | 2.8
|  |  |  | Office - Large |  |  |  |  | 2.9
|  |  |  | Office - Small |  |  |  |  | 2.9
|  |  |  | Religious |  |  |  |  | 3.5
|  |  |  | Restaurant |  |  |  |  | 1.5
|  |  |  | Retail - Large |  |  |  |  | 2.1
|  |  |  | Retail - Small |  |  |  |  | 2.3
|  |  |  | Warehouse |  |  |  |  | 2.9
|  |  |  | Nonresidential Average |  |  |  |  | 2.8
|  | >=310 and <=3300 |  | Nonresidential Average | CRI | <90 | Year | 2019 | 1 | 0.84
[8 empty] | 2020 | 1 | 0.56
[8 empty] | 2021 | 1 | 0.3
|  |  |  | Nonresidential Average |  | >=90 |  | 2019 | 1 | 0.89
[8 empty] | 2020 | 1 | 0.61
[8 empty] | 2021 | 1 | 0.35
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]) * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =(([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]) * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = (([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms])) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lumen Range | 250-309 |  |  |  |  | 15.6 | Y | Watts | Actual (if retrofit) or based on lumens of LED bulb installed
|  |  | 310-749 |  |  |  |  | 19.4
|  |  | 750-1049 |  |  |  |  | 29.5
|  |  | 1050-1489 |  |  |  |  | 37.4
|  |  | 1490-2600 |  |  |  |  | 52.9
|  |  | 2601-3300 |  |  |  |  | 101.7
|  |  | 3301-3999 |  |  |  |  | 133.7
|  |  | 4000-6000 |  |  |  |  | 197.5
| [WattsEE] | Product Type | ENERGY STAR | CRI | <90 | Lumen Range | 250-309 | 3.5 | Y | Watts | Actual wattage of LED purchased or installed
[7 empty] | 310-749 | 6.6
[7 empty] | 750-1049 | 11.2
[7 empty] | 1050-1489 | 15.9
[7 empty] | 1490-2600 | 25.6
[7 empty] | 2601-3300 | 36.9
[7 empty] | 3301-3999 | 45.6
[7 empty] | 4000-6000 | 62.5
[5 empty] | >=90 |  | 250-309 | 4
[7 empty] | 310-749 | 7.6
[7 empty] | 750-1049 | 12.9
[7 empty] | 1050-1489 | 18.1
[7 empty] | 1490-2600 | 29.2
[7 empty] | 2601-3300 | 42.2
[7 empty] | 3301-3999 | 52.1
[7 empty] | 4000-6000 | 71.4
|  |  | CEE Tier 2 |  | <90 |  | 250-309 | 2.9
[7 empty] | 310-749 | 5.6
[7 empty] | 750-1049 | 9.5
[7 empty] | 1050-1489 | 13.4
[7 empty] | 1490-2600 | 21.5
[7 empty] | 2601-3300 | 31.1
[7 empty] | 3301-3999 | 38.4
[7 empty] | 4000-6000 | 52.6
[5 empty] | >=90 |  | 250-309 | 3.5
[7 empty] | 310-749 | 6.6
[7 empty] | 750-1049 | 11.2
[7 empty] | 1050-1489 | 15.9
[7 empty] | 1490-2600 | 25.6
[7 empty] | 2601-3300 | 36.9
[7 empty] | 3301-3999 | 45.6
[7 empty] | 4000-6000 | 62.5
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  |  |  | 4630
|  |  | Education |  |  |  |  | 1877
|  |  | Exterior Lighting |  |  |  |  | 4676
|  |  | Grocery |  |  |  |  | 4663
|  |  | Health |  |  |  |  | 3806
|  |  | Hospital |  |  |  |  | 6520
|  |  | Industrial |  |  |  |  | 2850
|  |  | Lodging |  |  |  |  | 3061
|  |  | Multifamily |  |  |  |  | 3061
|  |  | Office - Large |  |  |  |  | 2920
|  |  | Office - Small |  |  |  |  | 2920
|  |  | Religious |  |  |  |  | 2412
|  |  | Restaurant |  |  |  |  | 5443
|  |  | Retail - Large |  |  |  |  | 4065
|  |  | Retail - Small |  |  |  |  | 3694
|  |  | Warehouse |  |  |  |  | 2920
|  |  | Nonresidential Average |  |  |  |  | 3065
|  |  | Unconditioned building |  |  |  |  | As specific building above
|  |  | Refrigerated Cases |  |  |  |  | As specific building above
|  |  | Freezer Cases |  |  |  |  | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 1 | N |  | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  |  |  | 1.14
|  |  | Education |  |  |  |  | 1.15
|  |  | Exterior Lighting |  |  |  |  | 1
|  |  | Grocery |  |  |  |  | 1.14
|  |  | Health |  |  |  |  | 1.18
|  |  | Hospital |  |  |  |  | 1.24
|  |  | Industrial |  |  |  |  | 1.02
|  |  | Lodging |  |  |  |  | 1.1
|  |  | Multifamily |  |  |  |  | 1.1
|  |  | Office - Large |  |  |  |  | 1.13
|  |  | Office - Small |  |  |  |  | 1.15
|  |  | Religious |  |  |  |  | 1.12
|  |  | Restaurant |  |  |  |  | 1.16
|  |  | Retail - Large |  |  |  |  | 1.14
|  |  | Retail - Small |  |  |  |  | 1.12
|  |  | Warehouse |  |  |  |  | 1.09
|  |  | Nonresidential Average |  |  |  |  | 1.13
|  |  | Unconditioned building |  |  |  |  | 1
|  |  | Refrigerated Cases |  |  |  |  | 1.29
|  |  | Freezer Cases |  |  |  |  | 1.5
| [ISR] | Program | Retail (Time of Sale) |  |  |  |  | 92% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit |  |  |  |  | 97%
| [MidLifeAdj] | Year of Savings | Before 2021 |  |  | Lumen Range | 250-309 | 100% | N | Percentage | Mid Life Adjustment to account for baseline shifting within the measure life to a CFL in 2020. This factor should be applied to the annual savings for years 2021 onwards for any measure installed prior to 2021.
[7 empty] | 310-749 | 100%
[7 empty] | 750-1049 | 100%
[7 empty] | 1050-1489 | 100%
[7 empty] | 1490-2600 | 100%
[7 empty] | 2601-3300 | 100%
[7 empty] | 3301-3999 | 100%
[7 empty] | 4000-6000 | 100%
|  |  | 2021 on | ENERGY STAR | CRI <90 |  | 250-309 | 100%
[7 empty] | 310-749 | 7%
[7 empty] | 750-1049 | 9%
[7 empty] | 1050-1489 | 11%
[7 empty] | 1490-2600 | 13%
[7 empty] | 2601-3300 | 8%
[7 empty] | 3301-3999 | 100%
[7 empty] | 4000-6000 | 100%
[5 empty] | CRI >90 |  | 250-309 | 100%
[7 empty] | 310-749 | 0%
[7 empty] | 750-1049 | 0%
[7 empty] | 1050-1489 | 0%
[7 empty] | 1490-2600 | 0%
[7 empty] | 2601-3300 | 0%
[7 empty] | 3301-3999 | 100%
[7 empty] | 4000-6000 | 100%
|  |  |  | CEE Tier 2 | CRI <90 |  | 250-309 | 100%
[7 empty] | 310-749 | 14%
[7 empty] | 750-1049 | 17%
[7 empty] | 1050-1489 | 20%
[7 empty] | 1490-2600 | 25%
[7 empty] | 2601-3300 | 16%
[7 empty] | 3301-3999 | 100%
[7 empty] | 4000-6000 | 100%
[5 empty] | CRI >90 |  | 250-309 | 100%
[7 empty] | 310-749 | 7%
[7 empty] | 750-1049 | 9%
[7 empty] | 1050-1489 | 11%
[7 empty] | 1490-2600 | 13%
[7 empty] | 2601-3300 | 8%
[7 empty] | 3301-3999 | 100%
[7 empty] | 4000-6000 | 100%
| [ΔkWhheatpenalty] | [7 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  |  |  | 0.36
|  |  | Education |  |  |  |  | 0.43
|  |  | Exterior Lighting |  |  |  |  | 0
|  |  | Grocery |  |  |  |  | 0.32
|  |  | Health |  |  |  |  | 0.55
|  |  | Hospital |  |  |  |  | 0.52
|  |  | Industrial |  |  |  |  | 0.37
|  |  | Lodging |  |  |  |  | 0.57
|  |  | Multifamily |  |  |  |  | 0.57
|  |  | Office - Large |  |  |  |  | 0.6
|  |  | Office - Small |  |  |  |  | 0.4
|  |  | Religious |  |  |  |  | 0.46
|  |  | Restaurant |  |  |  |  | 0.44
|  |  | Retail - Large |  |  |  |  | 0.43
|  |  | Retail - Small |  |  |  |  | 0.46
|  |  | Warehouse |  |  |  |  | 0.44
|  |  | Nonresidential Average |  |  |  |  | 0.43
|  |  | Unconditioned building |  |  |  |  | 0
|  |  | Refrigerated Cases |  |  |  |  | 0
|  |  | Freezer Cases |  |  |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump |  |  | 0
|  |  | Convenience |  |  |  |  | 0.16
|  |  | Education |  |  |  |  | 0.19
|  |  | Exterior Lighting |  |  |  |  | 0
|  |  | Grocery |  |  |  |  | 0.14
|  |  | Health |  |  |  |  | 0.24
|  |  | Hospital |  |  |  |  | 0.22
|  |  | Industrial |  |  |  |  | 0.16
|  |  | Lodging |  |  |  |  | 0.25
|  |  | Multifamily |  |  |  |  | 0.25
|  |  | Office - Large |  |  |  |  | 0.26
|  |  | Office - Small |  |  |  |  | 0.17
|  |  | Religious |  |  |  |  | 0.2
|  |  | Restaurant |  |  |  |  | 0.19
|  |  | Retail - Large |  |  |  |  | 0.19
|  |  | Retail - Small |  |  |  |  | 0.2
|  |  | Warehouse |  |  |  |  | 0.19
|  |  | Nonresidential Average |  |  |  |  | 0.19
|  |  | Unconditioned building |  |  |  |  | 0
|  |  | Refrigerated Cases |  |  |  |  | 0
|  |  | Freezer Cases |  |  |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  |  |  | 1.31
|  |  | Education |  |  |  |  | 1.67
|  |  | Exterior Lighting |  |  |  |  | 1
|  |  | Grocery |  |  |  |  | 1.22
|  |  | Health |  |  |  |  | 1.54
|  |  | Hospital |  |  |  |  | 1.53
|  |  | Industrial |  |  |  |  | 1.02
|  |  | Lodging |  |  |  |  | 1.15
|  |  | Multifamily |  |  |  |  | 1.15
|  |  | Office - Large |  |  |  |  | 1.24
|  |  | Office - Small |  |  |  |  | 1.45
|  |  | Religious |  |  |  |  | 1.32
|  |  | Restaurant |  |  |  |  | 1.39
|  |  | Retail - Large |  |  |  |  | 1.34
|  |  | Retail - Small |  |  |  |  | 1.39
|  |  | Warehouse |  |  |  |  | 1.43
|  |  | Nonresidential Average |  |  |  |  | 1.42
|  |  | Unconditioned building |  |  |  |  | 1
|  |  | Refrigerated Cases |  |  |  |  | 1.29
|  |  | Freezer Cases |  |  |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  |  |  | 100%
|  |  | Education |  |  |  |  | 62.3%
|  |  | Exterior Lighting |  |  |  |  | 0%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 96.1%
|  |  | Hospital |  |  |  |  | 100%
|  |  | Industrial |  |  |  |  | 91.8%
|  |  | Lodging |  |  |  |  | 19.8%
|  |  | Multifamily |  |  |  |  | 19.8%
|  |  | Office - Large |  |  |  |  | 48.4%
|  |  | Office - Small |  |  |  |  | 63.6%
|  |  | Religious |  |  |  |  | 66%
|  |  | Restaurant |  |  |  |  | 96.7%
|  |  | Retail - Large |  |  |  |  | 100%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 61.8%
|  |  | Nonresidential Average |  |  |  |  | 71.7%
|  |  | Unconditioned building |  |  |  |  | As specific building above
|  |  | Refrigerated Cases |  |  |  |  | As specific building above
|  |  | Freezer Cases |  |  |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  |  |  | 0.015
|  |  | Education |  |  |  |  | 0.018
|  |  | Exterior Lighting |  |  |  |  | 0
|  |  | Grocery |  |  |  |  | 0.014
|  |  | Health |  |  |  |  | 0.047
|  |  | Hospital |  |  |  |  | 0.022
|  |  | Industrial |  |  |  |  | 0.016
|  |  | Lodging |  |  |  |  | 0.024
|  |  | Multifamily |  |  |  |  | 0.024
|  |  | Office - Large |  |  |  |  | 0.026
|  |  | Office - Small |  |  |  |  | 0.017
|  |  | Religious |  |  |  |  | 0.02
|  |  | Restaurant |  |  |  |  | 0.019
|  |  | Retail - Large |  |  |  |  | 0.018
|  |  | Retail - Small |  |  |  |  | 0.019
|  |  | Warehouse |  |  |  |  | 0.019
|  |  | Nonresidential Average |  |  |  |  | 0.018
|  |  | Unconditioned building |  |  |  |  | 0
|  |  | Refrigerated Cases |  |  |  |  | 0
|  |  | Freezer Cases |  |  |  |  | 0
| [ΔTherms] | [7 empty] | C | Therms | Therm impact calculated above
| [HeatDays] | [6 empty] | 197 | N | Days | Heat season days per year

## LED Lamp - Specialty
LED Lamp - Specialty
| Measure Code: | NR-LTG-LEDS-VO3-190101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Agricultural Animal Housing and Warehousing | Bulb Type | Directional | 8.6055
|  | Convenience |  |  | 5.4272
|  | Education |  |  | 13.3873
|  | Exterior Lighting |  |  | 5.3738
|  | Grocery |  |  | 5.3888
|  | Health |  |  | 6.6022
|  | Hospital |  |  | 3.854
|  | Industrial |  |  | 8.8168
|  | Lodging |  |  | 8.2091
|  | Multifamily |  |  | 8.2091
|  | Office - Large |  |  | 8.6055
|  | Office - Small |  |  | 8.6055
|  | Religious |  |  | 10.4179
|  | Restaurant |  |  | 4.6166
|  | Retail - Large |  |  | 6.1815
|  | Retail - Small |  |  | 6.8024
|  | Warehouse |  |  | 8.6055
|  | Nonresidential Average |  |  | 8.1984
|  | Unconditioned building |  |  | As specific building above
|  | Refrigerated Cases |  |  | As specific building above
|  | Freezer Cases |  |  | As specific building above
|  | Agricultural Animal Housing and Warehousing |  | Decorative | 6.4106
|  | Convenience |  |  | 4.043
|  | Education |  |  | 9.9728
|  | Exterior Lighting |  |  | 4.0032
|  | Grocery |  |  | 4.0144
|  | Health |  |  | 4.9183
|  | Hospital |  |  | 2.871
|  | Industrial |  |  | 6.5681
|  | Lodging |  |  | 6.1153
|  | Multifamily |  |  | 6.1153
|  | Office - Large |  |  | 6.4106
|  | Office - Small |  |  | 6.4106
|  | Religious |  |  | 7.7608
|  | Restaurant |  |  | 3.4391
|  | Retail - Large |  |  | 4.6049
|  | Retail - Small |  |  | 5.0674
|  | Warehouse |  |  | 6.4106
|  | Nonresidential Average |  |  | 6.1073
|  | Unconditioned building |  |  | As specific building above
|  | Refrigerated Cases |  |  | As specific building above
|  | Freezer Cases |  |  | As specific building above
| Measure Cost: | [10 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Incremental Cost |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known | [6 empty] | Actual
|  | Unknown | Bulb Type | Directional | CRI | <90 | Product Type | ENERGY STAR | 2.42
[8 empty] | CEE Tier 2 | 13.58
[6 empty] | >=90 |  | ENERGY STAR | 2.26
[8 empty] | CEE Tier 2 | 13.18
|  |  |  | Decorative |  | <90 |  | ENERGY STAR | 3.95
[8 empty] | CEE Tier 2 | 4.28
[6 empty] | >=90 |  | ENERGY STAR | 5.02
[8 empty] | CEE Tier 2 | 5.41
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Dependent Variable Input 5 | Dependent Variable 5 Options | Life of Component | Cost
| Lumen Range | <310 and >3300 | Installation Location | Agricultural Animal Housing and Warehousing | Bulb Type | Directional |  |  |  |  | 1.5 | 5.38
|  |  |  | Convenience | [6 empty] | 0.9
|  |  |  | Education | [6 empty] | 2.3
|  |  |  | Exterior Lighting | [6 empty] | 0.9
|  |  |  | Grocery | [6 empty] | 0.9
|  |  |  | Health | [6 empty] | 1.1
|  |  |  | Hospital | [6 empty] | 0.7
|  |  |  | Industrial | [6 empty] | 1.5
|  |  |  | Lodging | [6 empty] | 1.4
|  |  |  | Multifamily | [6 empty] | 1.4
|  |  |  | Office - Large | [6 empty] | 1.5
|  |  |  | Office - Small | [6 empty] | 1.5
|  |  |  | Religious | [6 empty] | 1.8
|  |  |  | Restaurant | [6 empty] | 0.8
|  |  |  | Retail - Large | [6 empty] | 1.1
|  |  |  | Retail - Small | [6 empty] | 1.2
|  |  |  | Warehouse | [6 empty] | 1.5
|  |  |  | Nonresidential Average | [6 empty] | 1.4
|  |  |  | Agricultural Animal Housing and Warehousing |  | Decorative/Globe |  |  |  |  | 1.2575 | 3.55
|  |  |  | Convenience | [6 empty] | 0.79309
|  |  |  | Education | [6 empty] | 1.9563
|  |  |  | Exterior Lighting | [6 empty] | 0.78529
|  |  |  | Grocery | [6 empty] | 0.78748
|  |  |  | Health | [6 empty] | 0.96479
|  |  |  | Hospital | [6 empty] | 0.56319
|  |  |  | Industrial | [6 empty] | 1.2884
|  |  |  | Lodging | [6 empty] | 1.1996
|  |  |  | Multifamily | [6 empty] | 1.1996
|  |  |  | Office - Large | [6 empty] | 1.2575
|  |  |  | Office - Small | [6 empty] | 1.2575
|  |  |  | Religious | [6 empty] | 1.5224
|  |  |  | Restaurant | [6 empty] | 0.67463
|  |  |  | Retail - Large | [6 empty] | 0.90332
|  |  |  | Retail - Small | [6 empty] | 0.99404
|  |  |  | Warehouse | [6 empty] | 1.2575
|  |  |  | Nonresidential Average | [6 empty] | 1.198
|  | >=310 and <=3300 |  | Nonresidential Average |  | Directional | CRI | <90 | Year | 2019 | 1 | 4.22
[10 empty] | 2020 | 1 | 2.41
[10 empty] | 2021 | 1 | 0.88
[8 empty] | >=90 |  | 2019 | 1 | 3.84
[10 empty] | 2020 | 1 | 2.4
[10 empty] | 2021 | 1 | 0.88
[6 empty] | Decorative/Globe |  | <90 |  | 2019 | 1 | 2.37
[10 empty] | 2020 | 1 | 1.54
[10 empty] | 2021 | 1 | 0.72
[8 empty] | >=90 |  | 2019 | 1 | 2.47
[10 empty] | 2020 | 1 | 1.62
[10 empty] | 2021 | 1 | 0.77
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]) * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =(([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]) * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = (([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms])) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Dependent Variable Input 5 | Dependent Variable 45Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Bulb Type (Decorative) | 3-way | Lumen range | 250-449 | [6 empty] | 21.3 | N | Watts | Based on lumens of LED'Based on lumens of LED bulb installed and includes blend of incandescent/halogen , CFL and LED by weightings provided in table below . Note that when an IA net-to-gross (NTG) factor is determined for this measure, this blended baseline should be replaced with the Incandescent/Halogen baseline only.bulb installed and includes blend of incandescent/halogen , CFL and LED by weightings provided in table below . Note that when an IA net-to-gross (NTG) factor is determined for this measure, this blended baseline should be replaced with the Incandescent/Halogen baseline only.
[5 empty] | 450-799 | [6 empty] | 34.3
[5 empty] | 800-1099 | [6 empty] | 50.3
[5 empty] | 1100-1599 | [6 empty] | 63.4
[5 empty] | 1600-1999 | [6 empty] | 84.5
[5 empty] | 2000-2549 | [6 empty] | 106.7
[5 empty] | 2550-2999 | [6 empty] | 128.3
|  |  | Globe (medium and intermediate bases less than 750 lumens) |  | 90-179 | [6 empty] | 8.6
[5 empty] | 180-249 | [6 empty] | 13
[5 empty] | 250-349 | [6 empty] | 21.1
[5 empty] | 350-749 | [6 empty] | 33.6
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 70-89 | [6 empty] | 8.4
[5 empty] | 90-149 | [6 empty] | 12.5
[5 empty] | 150-299 | [6 empty] | 20.9
[5 empty] | 300-749 | [6 empty] | 33.3
|  |  | Globe (candelabra bases less than 1050 lumens) |  | 90-179 | [6 empty] | 8.6
[5 empty] | 180-249 | [6 empty] | 13
[5 empty] | 250-349 | [6 empty] | 21.1
[5 empty] | 350-499 | [6 empty] | 33.4
[5 empty] | 500-1049 | [6 empty] | 50.2
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra bases less than 1050 lumens) |  | 70-89 | [6 empty] | 8.4
[5 empty] | 90-149 | [6 empty] | 12.5
[5 empty] | 150-299 | [6 empty] | 20.8
[5 empty] | 300-499 | [6 empty] | 33.2
[5 empty] | 500-1049 | [6 empty] | 50.2
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) |  | 420-472 | [6 empty] | 33.9
[5 empty] | 473-524 | [6 empty] | 38
[5 empty] | 525-714 | [6 empty] | 42.4
[5 empty] | 715-937 | [6 empty] | 54.8
[5 empty] | 938-1259 | [6 empty] | 63.7
[5 empty] | 1260-1399 | [6 empty] | 76.1
[5 empty] | 1400-1739 | [6 empty] | 85.1
[5 empty] | 1740-2174 | [6 empty] | 102.5
[5 empty] | 2175-2624 | [6 empty] | 127.7
[5 empty] | 2625-2999 | [6 empty] | 151.2
[5 empty] | 3000-4500 | [6 empty] | 175
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" |  | 400-449 | [6 empty] | 33.7
[5 empty] | 450-499 | [6 empty] | 37.9
[5 empty] | 500-649 | [6 empty] | 42.2
[5 empty] | 650-1199 | [6 empty] | 55.2
|  |  | *ER30, BR30, BR40, or ER40 |  | 400-449 | [6 empty] | 34.1
[5 empty] | 450-499 | [6 empty] | 38.4
[5 empty] | 500-649 | [6 empty] | 42.6
|  |  | BR30, BR40, or ER40 |  | 650-1419 | [6 empty] | 55
|  |  | R20 |  | 400-449 | [6 empty] | 34.1
[5 empty] | 450-719 | [6 empty] | 38
|  |  | *All reflector lamps below lumen ranges specified above |  | 200-299 | [6 empty] | 17
[5 empty] | 300-399 | [6 empty] | 25.5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) |  | 250-309 | [6 empty] | 20.9
[5 empty] | 310-749 | [6 empty] | 24.8
[5 empty] | 750-1049 | [6 empty] | 36.8
[5 empty] | 1050-1489 | [6 empty] | 45.6
[5 empty] | 1490-2600 | [6 empty] | 61.8
| [WattsEE] | Bulb Type (Decorative) | 3-way | Product Type | ENERGY STAR | CRI | <90 | Lumen Range | 250-449 |  |  | 4.4 | Y | Watts | Actual wattage of LED pruchased/installed. If unknown, use default provided below
[9 empty] | 450-799 |  |  | 7.8
[9 empty] | 800-1099 |  |  | 11.9
[9 empty] | 1100-1599 |  |  | 16.9
[9 empty] | 1600-1999 |  |  | 22.5
[9 empty] | 2000-2549 |  |  | 28.4
[9 empty] | 2550-2999 |  |  | 34.7
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-749 |  |  | 8.5
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-749 |  |  | 8.1
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-499 |  |  | 6.5
[9 empty] | 500-1049 |  |  | 11.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-499 |  |  | 6.1
[9 empty] | 500-1049 |  |  | 11.9
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 6.4
[9 empty] | 473-524 |  |  | 7.1
[9 empty] | 525-714 |  |  | 8.9
[9 empty] | 715-937 |  |  | 11.8
[9 empty] | 938-1259 |  |  | 15.7
[9 empty] | 1260-1399 |  |  | 19
[9 empty] | 1400-1739 |  |  | 22.4
[9 empty] | 1740-2174 |  |  | 28
[9 empty] | 2175-2624 |  |  | 34.3
[9 empty] | 2625-2999 |  |  | 40.2
[9 empty] | 3000-4500 |  |  | 53.6
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
[9 empty] | 650-1199 |  |  | 13.2
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 14.8
|  |  | R20 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-719 |  |  | 8.4
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 3.6
[9 empty] | 300-399 |  |  | 5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 3.5
[9 empty] | 310-749 |  |  | 6.6
[9 empty] | 750-1049 |  |  | 11.2
[9 empty] | 1050-1489 |  |  | 15.9
[9 empty] | 1490-2600 |  |  | 25.6
|  | Bulb Type (Decorative) | 3-way |  |  |  | =>90 | Lumen Range | 250-449 |  |  | 5
[9 empty] | 450-799 |  |  | 8.9
[9 empty] | 800-1099 |  |  | 13.6
[9 empty] | 1100-1599 |  |  | 19.3
[9 empty] | 1600-1999 |  |  | 25.7
[9 empty] | 2000-2549 |  |  | 32.5
[9 empty] | 2550-2999 |  |  | 39.6
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-749 |  |  | 8.5
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-749 |  |  | 8.1
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-499 |  |  | 6.5
[9 empty] | 500-1049 |  |  | 11.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-499 |  |  | 6.1
[9 empty] | 500-1049 |  |  | 11.9
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 7.3
[9 empty] | 473-524 |  |  | 8.2
[9 empty] | 525-714 |  |  | 10.2
[9 empty] | 715-937 |  |  | 13.5
[9 empty] | 938-1259 |  |  | 18
[9 empty] | 1260-1399 |  |  | 21.8
[9 empty] | 1400-1739 |  |  | 25.7
[9 empty] | 1740-2174 |  |  | 32.1
[9 empty] | 2175-2624 |  |  | 39.3
[9 empty] | 2625-2999 |  |  | 46.1
[9 empty] | 3000-4500 |  |  | 61.5
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 7
[9 empty] | 450-499 |  |  | 7.8
[9 empty] | 500-649 |  |  | 9.4
[9 empty] | 650-1199 |  |  | 15.2
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 7
[9 empty] | 450-499 |  |  | 7.8
[9 empty] | 500-649 |  |  | 9.4
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 17
|  |  | R20 | [5 empty] | 400-449 |  |  | 7
[9 empty] | 450-719 |  |  | 9.6
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 4.1
[9 empty] | 300-399 |  |  | 5.7
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 4
[9 empty] | 310-749 |  |  | 7.6
[9 empty] | 750-1049 |  |  | 12.9
[9 empty] | 1050-1489 |  |  | 18.1
[9 empty] | 1490-2600 |  |  | 29.2
|  | Bulb Type (Decorative) | 3-way |  | CEE Tier 2 |  | <90 | Lumen Range | 250-449 |  |  | 3.7
[9 empty] | 450-799 |  |  | 6.6
[9 empty] | 800-1099 |  |  | 10
[9 empty] | 1100-1599 |  |  | 14.2
[9 empty] | 1600-1999 |  |  | 18.9
[9 empty] | 2000-2549 |  |  | 23.9
[9 empty] | 2550-2999 |  |  | 29.2
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.4
[9 empty] | 180-249 |  |  | 2.3
[9 empty] | 250-349 |  |  | 3.2
[9 empty] | 350-749 |  |  | 5.8
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 0.8
[9 empty] | 90-149 |  |  | 1.3
[9 empty] | 150-299 |  |  | 2.4
[9 empty] | 300-749 |  |  | 5.5
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.4
[9 empty] | 180-249 |  |  | 2.3
[9 empty] | 250-349 |  |  | 3.2
[9 empty] | 350-499 |  |  | 4.5
[9 empty] | 500-1049 |  |  | 8.2
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 0.8
[9 empty] | 90-149 |  |  | 1.3
[9 empty] | 150-299 |  |  | 2.4
[9 empty] | 300-499 |  |  | 4.2
[9 empty] | 500-1049 |  |  | 8.2
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 5.2
[9 empty] | 473-524 |  |  | 5.9
[9 empty] | 525-714 |  |  | 7.3
[9 empty] | 715-937 |  |  | 9.7
[9 empty] | 938-1259 |  |  | 12.9
[9 empty] | 1260-1399 |  |  | 15.6
[9 empty] | 1400-1739 |  |  | 18.5
[9 empty] | 1740-2174 |  |  | 23
[9 empty] | 2175-2624 |  |  | 28.2
[9 empty] | 2625-2999 |  |  | 33.1
[9 empty] | 3000-4500 |  |  | 44.1
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 5
[9 empty] | 450-499 |  |  | 5.6
[9 empty] | 500-649 |  |  | 6.8
[9 empty] | 650-1199 |  |  | 10.9
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 5
[9 empty] | 450-499 |  |  | 5.6
[9 empty] | 500-649 |  |  | 6.8
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 12.2
|  |  | R20 | [5 empty] | 400-449 |  |  | 5
[9 empty] | 450-719 |  |  | 6.9
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 2.9
[9 empty] | 300-399 |  |  | 4.1
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 2.9
[9 empty] | 310-749 |  |  | 5.6
[9 empty] | 750-1049 |  |  | 9.5
[9 empty] | 1050-1489 |  |  | 13.4
[9 empty] | 1490-2600 |  |  | 21.5
|  | Bulb Type (Decorative) | 3-way |  |  |  | =>90 | Lumen Range | 250-449 |  |  | 4.4
[9 empty] | 450-799 |  |  | 7.8
[9 empty] | 800-1099 |  |  | 11.9
[9 empty] | 1100-1599 |  |  | 16.9
[9 empty] | 1600-1999 |  |  | 22.5
[9 empty] | 2000-2549 |  |  | 28.4
[9 empty] | 2550-2999 |  |  | 34.7
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.7
[9 empty] | 180-249 |  |  | 2.7
[9 empty] | 250-349 |  |  | 3.7
[9 empty] | 350-749 |  |  | 6.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 1
[9 empty] | 90-149 |  |  | 1.5
[9 empty] | 150-299 |  |  | 2.8
[9 empty] | 300-749 |  |  | 6.6
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.7
[9 empty] | 180-249 |  |  | 2.7
[9 empty] | 250-349 |  |  | 3.7
[9 empty] | 350-499 |  |  | 5.3
[9 empty] | 500-1049 |  |  | 9.7
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 1
[9 empty] | 90-149 |  |  | 1.5
[9 empty] | 150-299 |  |  | 2.8
[9 empty] | 300-499 |  |  | 5
[9 empty] | 500-1049 |  |  | 9.7
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 6.4
[9 empty] | 473-524 |  |  | 7.1
[9 empty] | 525-714 |  |  | 8.9
[9 empty] | 715-937 |  |  | 11.8
[9 empty] | 938-1259 |  |  | 15.7
[9 empty] | 1260-1399 |  |  | 19
[9 empty] | 1400-1739 |  |  | 22.4
[9 empty] | 1740-2174 |  |  | 28
[9 empty] | 2175-2624 |  |  | 34.3
[9 empty] | 2625-2999 |  |  | 40.2
[9 empty] | 3000-4500 |  |  | 53.6
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
[9 empty] | 650-1199 |  |  | 13.2
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 14.8
|  |  | R20 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-719 |  |  | 8.4
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 3.6
[9 empty] | 300-399 |  |  | 5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 3.5
[9 empty] | 310-749 |  |  | 6.6
[9 empty] | 750-1049 |  |  | 11.2
[9 empty] | 1050-1489 |  |  | 15.9
[9 empty] | 1490-2600 |  |  | 25.6
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience | [8 empty] | 4630
|  |  | Education | [8 empty] | 1877
|  |  | Exterior Lighting | [8 empty] | 4676
|  |  | Grocery | [8 empty] | 4663
|  |  | Health | [8 empty] | 3806
|  |  | Hospital | [8 empty] | 6520
|  |  | Industrial | [8 empty] | 2850
|  |  | Lodging | [8 empty] | 3061
|  |  | Multifamily | [8 empty] | 3061
|  |  | Office - Large | [8 empty] | 2920
|  |  | Office - Small | [8 empty] | 2920
|  |  | Religious | [8 empty] | 2412
|  |  | Restaurant | [8 empty] | 5443
|  |  | Retail - Large | [8 empty] | 4065
|  |  | Retail - Small | [8 empty] | 3694
|  |  | Warehouse | [8 empty] | 2920
|  |  | Nonresidential Average | [8 empty] | 3065
|  |  | Unconditioned building | [8 empty] | As specific building above
|  |  | Refrigerated Cases | [8 empty] | As specific building above
|  |  | Freezer Cases | [8 empty] | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 1 | N |  | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience | [8 empty] | 1.14
|  |  | Education | [8 empty] | 1.15
|  |  | Exterior Lighting | [8 empty] | 1
|  |  | Grocery | [8 empty] | 1.14
|  |  | Health | [8 empty] | 1.18
|  |  | Hospital | [8 empty] | 1.24
|  |  | Industrial | [8 empty] | 1.02
|  |  | Lodging | [8 empty] | 1.1
|  |  | Multifamily | [8 empty] | 1.1
|  |  | Office - Large | [8 empty] | 1.13
|  |  | Office - Small | [8 empty] | 1.15
|  |  | Religious | [8 empty] | 1.12
|  |  | Restaurant | [8 empty] | 1.16
|  |  | Retail - Large | [8 empty] | 1.14
|  |  | Retail - Small | [8 empty] | 1.12
|  |  | Warehouse | [8 empty] | 1.09
|  |  | Nonresidential Average | [8 empty] | 1.13
|  |  | Unconditioned building | [8 empty] | 1
|  |  | Refrigerated Cases | [8 empty] | 1.29
|  |  | Freezer Cases | [8 empty] | 1.5
| [ISR] | Program | Retail (Time of Sale) | [8 empty] | 92% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit | [8 empty] | 97%
| [MidLifeAdj] | Year | Before 2021 | [8 empty] | 100% | N | Percentage | Mid Life Adjustment to account for baseline shifting within the measure life to a CFL in 2020. This factor should be applied to the annual savings for years 2020 onwards for any measure installed prior to 2020.
|  |  | From 1/1/2021 | Bulb Type (Decorative) | 3-way | Product Type | ENERGY STAR | CRI | <90 | Lumen Range | 250-449 | 4%
[11 empty] | 450-799 | 4%
[11 empty] | 800-1099 | 4%
[11 empty] | 1100-1599 | 5%
[11 empty] | 1600-1999 | 5%
[11 empty] | 2000-2549 | 5%
[11 empty] | 2550-2999 | 5%
[5 empty] | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 | 6%
[11 empty] | 180-249 | 6%
[11 empty] | 250-349 | 5%
[11 empty] | 350-749 | 6%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 | 3%
[11 empty] | 90-149 | 3%
[11 empty] | 150-299 | 4%
[11 empty] | 300-749 | 6%
[5 empty] | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 | 6%
[11 empty] | 180-249 | 6%
[11 empty] | 250-349 | 5%
[11 empty] | 350-499 | 4%
[11 empty] | 500-1049 | 6%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 | 3%
[11 empty] | 90-149 | 3%
[11 empty] | 150-299 | 4%
[11 empty] | 300-499 | 4%
[11 empty] | 500-1049 | 6%
|  |  |  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 | 4%
[11 empty] | 473-524 | 4%
[11 empty] | 525-714 | 4%
[11 empty] | 715-937 | 5%
[11 empty] | 938-1259 | 5%
[11 empty] | 1260-1399 | 6%
[11 empty] | 1400-1739 | 6%
[11 empty] | 1740-2174 | 6%
[11 empty] | 2175-2624 | 6%
[11 empty] | 2625-2999 | 6%
[11 empty] | 3000-4500 | 7%
[5 empty] | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 | 4%
[11 empty] | 450-499 | 4%
[11 empty] | 500-649 | 4%
[11 empty] | 650-1199 | 5%
[5 empty] | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 | 4%
[11 empty] | 450-499 | 4%
[11 empty] | 500-649 | 4%
[5 empty] | BR30, BR40, or ER 40 | [5 empty] | 650-1419 | 6%
[5 empty] | R20 | [5 empty] | 400-449 | 4%
[11 empty] | 450-719 | 5%
[5 empty] | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 | 4%
[11 empty] | 300-399 | 4%
|  |  |  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 | 3%
[11 empty] | 310-749 | 5%
[11 empty] | 750-1049 | 6%
[11 empty] | 1050-1489 | 8%
[11 empty] | 1490-2600 | 10%
|  |  |  | Bulb Type (Decorative) | 3-way |  |  |  | =>90 | Lumen Range | 250-449 | 0%
[11 empty] | 450-799 | 0%
[11 empty] | 800-1099 | 0%
[11 empty] | 1100-1599 | 0%
[11 empty] | 1600-1999 | 0%
[11 empty] | 2000-2549 | 0%
[11 empty] | 2550-2999 | 0%
[5 empty] | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 | 6%
[11 empty] | 180-249 | 6%
[11 empty] | 250-349 | 5%
[11 empty] | 350-749 | 6%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 | 3%
[11 empty] | 90-149 | 3%
[11 empty] | 150-299 | 4%
[11 empty] | 300-749 | 6%
[5 empty] | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 | 6%
[11 empty] | 180-249 | 6%
[11 empty] | 250-349 | 5%
[11 empty] | 350-499 | 4%
[11 empty] | 500-1049 | 6%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 | 3%
[11 empty] | 90-149 | 3%
[11 empty] | 150-299 | 4%
[11 empty] | 300-499 | 4%
[11 empty] | 500-1049 | 6%
|  |  |  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 | 0%
[11 empty] | 473-524 | 0%
[11 empty] | 525-714 | 1%
[11 empty] | 715-937 | 1%
[11 empty] | 938-1259 | 1%
[11 empty] | 1260-1399 | 1%
[11 empty] | 1400-1739 | 1%
[11 empty] | 1740-2174 | 1%
[11 empty] | 2175-2624 | 1%
[11 empty] | 2625-2999 | 1%
[11 empty] | 3000-4500 | 1%
[5 empty] | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 | 0%
[11 empty] | 450-499 | 0%
[11 empty] | 500-649 | 0%
[11 empty] | 650-1199 | 1%
[5 empty] | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 | 0%
[11 empty] | 450-499 | 0%
[11 empty] | 500-649 | 0%
[5 empty] | BR30, BR40, or ER 40 | [5 empty] | 650-1419 | 1%
[5 empty] | R20 | [5 empty] | 400-449 | 0%
[11 empty] | 450-719 | 1%
[5 empty] | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 | 1%
[11 empty] | 300-399 | 0%
|  |  |  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 | 0%
[11 empty] | 310-749 | 0%
[11 empty] | 750-1049 | 0%
[11 empty] | 1050-1489 | 0%
[11 empty] | 1490-2600 | 0%
|  |  |  | Bulb Type (Decorative) | 3-way |  | CEE Tier 2 |  | <90 | Lumen Range | 250-449 | 7%
[11 empty] | 450-799 | 8%
[11 empty] | 800-1099 | 9%
[11 empty] | 1100-1599 | 10%
[11 empty] | 1600-1999 | 10%
[11 empty] | 2000-2549 | 10%
[11 empty] | 2550-2999 | 11%
[5 empty] | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 | 14%
[11 empty] | 180-249 | 15%
[11 empty] | 250-349 | 13%
[11 empty] | 350-749 | 15%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 | 8%
[11 empty] | 90-149 | 8%
[11 empty] | 150-299 | 9%
[11 empty] | 300-749 | 14%
[5 empty] | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 | 14%
[11 empty] | 180-249 | 15%
[11 empty] | 250-349 | 13%
[11 empty] | 350-499 | 11%
[11 empty] | 500-1049 | 14%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 | 8%
[11 empty] | 90-149 | 8%
[11 empty] | 150-299 | 9%
[11 empty] | 300-499 | 11%
[11 empty] | 500-1049 | 14%
|  |  |  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 | 8%
[11 empty] | 473-524 | 8%
[11 empty] | 525-714 | 9%
[11 empty] | 715-937 | 9%
[11 empty] | 938-1259 | 11%
[11 empty] | 1260-1399 | 11%
[11 empty] | 1400-1739 | 12%
[11 empty] | 1740-2174 | 12%
[11 empty] | 2175-2624 | 12%
[11 empty] | 2625-2999 | 12%
[11 empty] | 3000-4500 | 14%
[5 empty] | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 | 7%
[11 empty] | 450-499 | 7%
[11 empty] | 500-649 | 8%
[11 empty] | 650-1199 | 10%
[5 empty] | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 | 7%
[11 empty] | 450-499 | 7%
[11 empty] | 500-649 | 8%
[5 empty] | BR30, BR40, or ER 40 | [5 empty] | 650-1419 | 12%
[5 empty] | R20 | [5 empty] | 400-449 | 7%
[11 empty] | 450-719 | 9%
[5 empty] | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 | 9%
[11 empty] | 300-399 | 8%
|  |  |  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 | 6%
[11 empty] | 310-749 | 10%
[11 empty] | 750-1049 | 12%
[11 empty] | 1050-1489 | 15%
[11 empty] | 1490-2600 | 19%
|  |  |  | Bulb Type (Decorative) | 3-way |  |  |  | =>90 | Lumen Range | 250-449 | 4%
[11 empty] | 450-799 | 4%
[11 empty] | 800-1099 | 4%
[11 empty] | 1100-1599 | 5%
[11 empty] | 1600-1999 | 5%
[11 empty] | 2000-2549 | 5%
[11 empty] | 2550-2999 | 5%
[5 empty] | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 | 11%
[11 empty] | 180-249 | 12%
[11 empty] | 250-349 | 10%
[11 empty] | 350-749 | 12%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 | 6%
[11 empty] | 90-149 | 6%
[11 empty] | 150-299 | 7%
[11 empty] | 300-749 | 11%
[5 empty] | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 | 11%
[11 empty] | 180-249 | 12%
[11 empty] | 250-349 | 10%
[11 empty] | 350-499 | 9%
[11 empty] | 500-1049 | 11%
[5 empty] | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 | 6%
[11 empty] | 90-149 | 6%
[11 empty] | 150-299 | 7%
[11 empty] | 300-499 | 8%
[11 empty] | 500-1049 | 11%
|  |  |  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 | 4%
[11 empty] | 473-524 | 4%
[11 empty] | 525-714 | 4%
[11 empty] | 715-937 | 5%
[11 empty] | 938-1259 | 5%
[11 empty] | 1260-1399 | 6%
[11 empty] | 1400-1739 | 6%
[11 empty] | 1740-2174 | 6%
[11 empty] | 2175-2624 | 6%
[11 empty] | 2625-2999 | 6%
[11 empty] | 3000-4500 | 7%
[5 empty] | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 | 4%
[11 empty] | 450-499 | 4%
[11 empty] | 500-649 | 4%
[11 empty] | 650-1199 | 5%
[5 empty] | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 | 4%
[11 empty] | 450-499 | 4%
[11 empty] | 500-649 | 4%
[5 empty] | BR30, BR40, or ER 40 | [5 empty] | 650-1419 | 6%
[5 empty] | R20 | [5 empty] | 400-449 | 4%
[11 empty] | 450-719 | 5%
[5 empty] | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 | 4%
[11 empty] | 300-399 | 4%
|  |  |  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 | 3%
[11 empty] | 310-749 | 5%
[11 empty] | 750-1049 | 6%
[11 empty] | 1050-1489 | 8%
[11 empty] | 1490-2600 | 10%
| [ΔkWhheatpenalty] | [11 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | [6 empty] | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience | [8 empty] | 0.36
|  |  | Education | [8 empty] | 0.43
|  |  | Exterior Lighting | [8 empty] | 0
|  |  | Grocery | [8 empty] | 0.32
|  |  | Health | [8 empty] | 0.55
|  |  | Hospital | [8 empty] | 0.52
|  |  | Industrial | [8 empty] | 0.37
|  |  | Lodging | [8 empty] | 0.57
|  |  | Multifamily | [8 empty] | 0.57
|  |  | Office - Large | [8 empty] | 0.6
|  |  | Office - Small | [8 empty] | 0.4
|  |  | Religious | [8 empty] | 0.46
|  |  | Restaurant | [8 empty] | 0.44
|  |  | Retail - Large | [8 empty] | 0.43
|  |  | Retail - Small | [8 empty] | 0.46
|  |  | Warehouse | [8 empty] | 0.44
|  |  | Nonresidential Average | [8 empty] | 0.43
|  |  | Unconditioned building | [8 empty] | 0
|  |  | Refrigerated Cases | [8 empty] | 0
|  |  | Freezer Cases | [8 empty] | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | [6 empty] | 0
|  |  | Convenience | [8 empty] | 0.16
|  |  | Education | [8 empty] | 0.19
|  |  | Exterior Lighting | [8 empty] | 0
|  |  | Grocery | [8 empty] | 0.14
|  |  | Health | [8 empty] | 0.24
|  |  | Hospital | [8 empty] | 0.22
|  |  | Industrial | [8 empty] | 0.16
|  |  | Lodging | [8 empty] | 0.25
|  |  | Multifamily | [8 empty] | 0.25
|  |  | Office - Large | [8 empty] | 0.26
|  |  | Office - Small | [8 empty] | 0.17
|  |  | Religious | [8 empty] | 0.2
|  |  | Restaurant | [8 empty] | 0.19
|  |  | Retail - Large | [8 empty] | 0.19
|  |  | Retail - Small | [8 empty] | 0.2
|  |  | Warehouse | [8 empty] | 0.19
|  |  | Nonresidential Average | [8 empty] | 0.19
|  |  | Unconditioned building | [8 empty] | 0
|  |  | Refrigerated Cases | [8 empty] | 0
|  |  | Freezer Cases | [8 empty] | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience | [8 empty] | 1.31
|  |  | Education | [8 empty] | 1.67
|  |  | Exterior Lighting | [8 empty] | 1
|  |  | Grocery | [8 empty] | 1.22
|  |  | Health | [8 empty] | 1.54
|  |  | Hospital | [8 empty] | 1.53
|  |  | Industrial | [8 empty] | 1.02
|  |  | Lodging | [8 empty] | 1.15
|  |  | Multifamily | [8 empty] | 1.15
|  |  | Office - Large | [8 empty] | 1.24
|  |  | Office - Small | [8 empty] | 1.45
|  |  | Religious | [8 empty] | 1.32
|  |  | Restaurant | [8 empty] | 1.39
|  |  | Retail - Large | [8 empty] | 1.34
|  |  | Retail - Small | [8 empty] | 1.39
|  |  | Warehouse | [8 empty] | 1.43
|  |  | Nonresidential Average | [8 empty] | 1.42
|  |  | Unconditioned building | [8 empty] | 1
|  |  | Refrigerated Cases | [8 empty] | 1.29
|  |  | Freezer Cases | [8 empty] | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience | [8 empty] | 100%
|  |  | Education | [8 empty] | 62.3%
|  |  | Exterior Lighting | [8 empty] | 0%
|  |  | Grocery | [8 empty] | 100%
|  |  | Health | [8 empty] | 96.1%
|  |  | Hospital | [8 empty] | 100%
|  |  | Industrial | [8 empty] | 91.8%
|  |  | Lodging | [8 empty] | 19.8%
|  |  | Multifamily | [8 empty] | 19.8%
|  |  | Office - Large | [8 empty] | 48.4%
|  |  | Office - Small | [8 empty] | 63.6%
|  |  | Religious | [8 empty] | 66%
|  |  | Restaurant | [8 empty] | 96.7%
|  |  | Retail - Large | [8 empty] | 100%
|  |  | Retail - Small | [8 empty] | 100%
|  |  | Warehouse | [8 empty] | 61.8%
|  |  | Nonresidential Average | [8 empty] | 71.7%
|  |  | Unconditioned building | [8 empty] | As specific building above
|  |  | Refrigerated Cases | [8 empty] | As specific building above
|  |  | Freezer Cases | [8 empty] | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience | [8 empty] | 0.015
|  |  | Education | [8 empty] | 0.018
|  |  | Exterior Lighting | [8 empty] | 0
|  |  | Grocery | [8 empty] | 0.014
|  |  | Health | [8 empty] | 0.047
|  |  | Hospital | [8 empty] | 0.022
|  |  | Industrial | [8 empty] | 0.016
|  |  | Lodging | [8 empty] | 0.024
|  |  | Multifamily | [8 empty] | 0.024
|  |  | Office - Large | [8 empty] | 0.026
|  |  | Office - Small | [8 empty] | 0.017
|  |  | Religious | [8 empty] | 0.02
|  |  | Restaurant | [8 empty] | 0.019
|  |  | Retail - Large | [8 empty] | 0.018
|  |  | Retail - Small | [8 empty] | 0.019
|  |  | Warehouse | [8 empty] | 0.019
|  |  | Nonresidential Average | [8 empty] | 0.018
|  |  | Unconditioned building | [8 empty] | 0
|  |  | Refrigerated Cases | [8 empty] | 0
|  |  | Freezer Cases | [8 empty] | 0
| [ΔTherms] | [11 empty] | C | Therms | Therm impact calculated above
| [HeatDays] | [10 empty] | 197 | N | Days | Heat season days per year

## LED Fixtures
LED Fixtures
| Measure Code: | NR-LTG-LDFX-V03-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
13
| Measure Cost: | Please see reference tables in 3.4.5 |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| O&M Cost: | Please see reference tables in 3.4.5
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR] * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF] * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms]) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
| [MidLifeAdj] |  |  | =(([WattsT8base] -[WattsEE])/([WattsBase] - [WattsEE]))
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Category | LED Downlight Fixtures | Description | 40% CFL 26W Pin Based & 60% PAR30/38 | 54.3 | N | Watts | Input wattage of the existing or baseline system.
|  |  | LED Interior Directional |  | 10% CMH PAR38 & 90% Halogen PAR38 | 60.4
[5 empty] | 40% CFL 42W Pin Base & 60% Halogen PAR38 | 17.7
|  |  | LED Display Case |  | 50% 2’T5 Linear & 50% 50W Halogen | 36.2/ft
[5 empty] | 50% 2’T5 Linear & 50% 50W Halogen | 36.2/ft
[5 empty] | 5’T8 | 15.2/ft
[5 empty] | 6’T12HO | 18.7/ft
|  |  | LED Linear Replacement Lamps |  | F17T8 Standard Lamp - 2 foot | 15
[5 empty] | F32T8 Standard Lamp - 4 foot | 28.2
[5 empty] | F32T8/HO Standard Lamp - 4 foot | 4.2
|  |  | LED Troffers |  | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
[5 empty] | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
[5 empty] | 18:82;4-Lamp 34w T12 (BF < 0.88): 4-Lamp 32w T8 (BF < 0.88) | 118.3
[5 empty] | 18:82; 1-Lamp 34w T12 (BF <0.88) : 1-Lamp 32w T8 (BF <0.91) | 29.5
[5 empty] | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
|  |  | LED Linear Ambiant Fixtures |  | 18:82; 1-Lamp 34w T12 (BF <0.88) : 1-Lamp 32w T8 (BF <0.91) | 29.5
[5 empty] | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
[5 empty] | T5HO 2L-F54T5HO - 4' | 120
[5 empty] | T5HO 3L-F54T5HO - 4' | 180
|  |  | LED High & Low Bay Fixtures |  | 3-Lamp T8HO Low-Bay | 157
[5 empty] | 4-Lamp T8HO High-Bay | 196
[5 empty] | 6-Lamp T8HO High-Bay | 294
[5 empty] | 8-Lamp T8HO High-Bay | 392
|  |  | LED Agricultural Interior Fixtures |  | 25% 73 Watt EISA Inc, 75% 1L T8 | 42
[5 empty] | 25% 146 Watt EISA Inc, 75% 2L T8 | 81
[5 empty] | 25% 217 Watt EISA Inc, 75% 3L T8 | 121
[5 empty] | 25% 292 Watt EISA Inc, 75% 4L T8 | 159
[5 empty] | 200W Pulse Start Metal Halide | 227.3
[5 empty] | 320W Pulse Start Metal Halide | 363.6
[5 empty] | 350W Pulse Start Metal Halide | 397.7
[5 empty] | (2) 320W Pulse Start Metal Halide | 727.3
|  |  | LED Exterior Fictures |  | 100W Metal Halide | 113.6
[5 empty] | 175W Pulse Start Metal Halide | 198.9
[5 empty] | 250W Pulse Start Metal Halide | 284.1
[5 empty] | 400W Pulse Start Metal Halide | 454.5
| [WattsEE] | Category | LED Downlight Fixtures | Description | LED Recessed, Surface, Pendant Downlights | 17.6 | N | Watts | Actual wattage of LED fixture purchased / installed. If unknown, use default provided in
|  |  | LED Interior Directional |  | LED Track Lighting | 12.2
[5 empty] | LED Wall-Wash Fixtures | 8.3
|  |  | LED Display Case |  | LED Display Case Light Fixture | 7.1
[5 empty] | LED Undercabinet Shelf-Mounted Task Light Fixtures | 7.1
[5 empty] | LED Refrigerated Case Light, Horizontal or Vertical | 7.6
[5 empty] | LED Freezer Case Light, Horizontal or Vertical | 7.6667
|  |  | LED Linear Replacement Lamps |  | T8 LED Replacement Lamp (TLED), < 1200 lumens | 8.9
[5 empty] | T8 LED Replacement Lamp (TLED), 1200-2400 lumens | 15.8
[5 empty] | T8 LED Replacement Lamp (TLED), 2401-4000 lumens | 22.9
|  |  | LED Troffers |  | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 25.4
[5 empty] | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 36.7
[5 empty] | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 33.3
[5 empty] | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 44.8
[5 empty] | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 57.2
[5 empty] | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 21.8
[5 empty] | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 33.7
[5 empty] | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 43.3
|  |  | LED Linear Ambiant Fixtures |  | LED Surface & Suspended Linear Fixture, <= 3000 lumens | 19.5
[5 empty] | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 32.1
[5 empty] | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 43.5
[5 empty] | LED Surface & Suspended Linear Fixture, 6001-7500 lumens | 56.3
[5 empty] | LED Surface & Suspended Linear Fixture, 7501-15,000 lumens | 82.4
|  |  | LED High & Low Bay Fixtures |  | LED Low-Bay Fixtures, <= 10,000 lumens | 61.6
[5 empty] | LED High-Bay Fixtures, 10,001-15,000 lumens | 99.5
[5 empty] | LED High-Bay Fixtures, 15,001-20,000 lumens | 140.2
[5 empty] | LED High-Bay Fixtures, 20,001-30,000 lumens | 193.8
|  |  | LED Agricultural Interior Fixtures |  | LED Ag Interior Fixtures, <= 2,000 lumens | 12.9
[5 empty] | LED Ag Interior Fixtures, 2,001-4,000 lumens | 29.7
[5 empty] | LED Ag Interior Fixtures, 4,001-6,000 lumens | 45.1
[5 empty] | LED Ag Interior Fixtures, 6,001-8,000 lumens | 59.7
[5 empty] | LED Ag Interior Fixtures, 8,001-12,000 lumens | 84.9
[5 empty] | LED Ag Interior Fixtures, 12,001-16,000 lumens | 113.9
[5 empty] | LED Ag Interior Fixtures, 16,001-20,000 lumens | 143.7
[5 empty] | LED Ag Interior Fixtures, 20,001-30,000 lumens | 193.8
|  |  | LED Exterior Fictures |  | LED Exterior Fixtures, <= 5,000 lumens | 34.1
[5 empty] | LED Exterior Fixtures, 5,001-10,000 lumens | 67.2
[5 empty] | LED Exterior Fixtures, 10,001-15,000 lumens | 108.8
[5 empty] | LED Exterior Fixtures, 15,001-30,000 lumens | 183.9
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.15
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 1.14
|  |  | Health |  |  | 1.18
|  |  | Hospital |  |  | 1.24
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.1
|  |  | Multifamily |  |  | 1.1
|  |  | Office - Large |  |  | 1.13
|  |  | Office - Small |  |  | 1.15
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1.16
|  |  | Retail - Large |  |  | 1.14
|  |  | Retail - Small |  |  | 1.12
|  |  | Warehouse |  |  | 1.09
|  |  | Nonresidential Average |  |  | 1.13
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] | Program Type | Time of Sale |  |  | 95% | N |  | In Servce Rate or the percentage of units rebated that get installed
|  |  | Retrofit |  |  | 100%
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.43
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.32
|  |  | Health |  |  | 0.55
|  |  | Hospital |  |  | 0.52
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.57
|  |  | Multifamily |  |  | 0.57
|  |  | Office - Large |  |  | 0.6
|  |  | Office - Small |  |  | 0.4
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0.44
|  |  | Retail - Large |  |  | 0.43
|  |  | Retail - Small |  |  | 0.46
|  |  | Warehouse |  |  | 0.44
|  |  | Nonresidential Average |  |  | 0.43
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.19
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.14
|  |  | Health |  |  | 0.24
|  |  | Hospital |  |  | 0.22
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.25
|  |  | Multifamily |  |  | 0.25
|  |  | Office - Large |  |  | 0.26
|  |  | Office - Small |  |  | 0.17
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0.19
|  |  | Retail - Large |  |  | 0.19
|  |  | Retail - Small |  |  | 0.2
|  |  | Warehouse |  |  | 0.19
|  |  | Nonresidential Average |  |  | 0.19
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [MidLifeAdj] | [5 empty] | C |  | A midlife savings adjustment should be applied to any measure with a blended T12:Standard T8 baseline. The adjustment should occur in 2020 to account for the baseline lamp replacement assumption changing from a blended 82/18 Standard T8/T12 to 100% Standard T8 by 2020.
| [WattsT8Base] | Category | LED Linear Replacement Lamps | Description | LED 4' Linear Replacement Lamp | 32 | N | Watts | Input wattage of the existing system based on 100% T8 fixture
[5 empty] | LED 2' Linear Replacement Lamp | 17
|  |  | LED Troffers |  | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 56.96
[5 empty] | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 84.48
[5 empty] | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 56.96
[5 empty] | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 84.48
[5 empty] | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 113
[5 empty] | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 29.12
[5 empty] | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 56.96
[5 empty] | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 84.48
|  |  | LED Linear Ambient Fixtures |  | LED Surface & Suspended Linear Fixture, ≤ 3000 lumens | 29.12
[5 empty] | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 56.96
[5 empty] | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 84.48
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.67
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.22
|  |  | Health |  |  | 1.54
|  |  | Hospital |  |  | 1.53
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.15
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.24
|  |  | Office - Small |  |  | 1.45
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.39
|  |  | Retail - Large |  |  | 1.34
|  |  | Retail - Small |  |  | 1.39
|  |  | Warehouse |  |  | 1.43
|  |  | Nonresidential Average |  |  | 1.42
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 62.3%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 96.1%
|  |  | Hospital |  |  | 100%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 19.8%
|  |  | Multifamily |  |  | 19.8%
|  |  | Office - Large |  |  | 48.4%
|  |  | Office - Small |  |  | 63.6%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 96.7%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 71.7%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.018
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.014
|  |  | Health |  |  | 0.047
|  |  | Hospital |  |  | 0.022
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.024
|  |  | Multifamily |  |  | 0.024
|  |  | Office - Large |  |  | 0.026
|  |  | Office - Small |  |  | 0.017
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0.019
|  |  | Retail - Large |  |  | 0.018
|  |  | Retail - Small |  |  | 0.019
|  |  | Warehouse |  |  | 0.019
|  |  | Nonresidential Average |  |  | 0.018
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## T5 HO Fix. and Lamp and Ballast
T5 HO Fix. and Lamp and Ballast
| Measure Code: | NR-LTG-T5HO-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
100
| O&M Cost: | Please see reference tables in 3.4.6
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lamp Type | 3-Lamp T5 High-Bay | Baseline Description | 200 Watt Pulse Start Metal-Halide | 227 | Y | Watts | Actual (if retrofit) or based on lumens of CFL bulb installed
|  |  | 4-Lamp T5 High-Bay |  | 320 Watt Pulse Start Metal-Halide | 364
|  |  | 6-Lamp T5 High-Bay |  | 400 Watt Pulse Start Metal-Halide | 455
|  |  | 8-Lamp T5 High-Bay |  | 750 Watt Pulse Start Metal-Halide | 825
| [WattsEE] | Lamp Type | 3-Lamp T5 High-Bay |  |  | 176 | Y | Watts | Actual wattage of CFL purchased or installed
|  |  | 4-Lamp T5 High-Bay |  |  | 235
|  |  | 6-Lamp T5 High-Bay |  |  | 352
|  |  | 8-Lamp T5 High-Bay |  |  | 470
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.15
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 1.14
|  |  | Health |  |  | 1.18
|  |  | Hospital |  |  | 1.24
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.1
|  |  | Multifamily |  |  | 1.1
|  |  | Office - Large |  |  | 1.13
|  |  | Office - Small |  |  | 1.15
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1.16
|  |  | Retail - Large |  |  | 1.14
|  |  | Retail - Small |  |  | 1.12
|  |  | Warehouse |  |  | 1.09
|  |  | Nonresidential Average |  |  | 1.13
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] | Form completed? | Yes |  |  | 100% | N |  | In Servce Rate or the percentage of units rebated that get installed
|  |  | No |  |  | 98%
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.43
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.32
|  |  | Health |  |  | 0.55
|  |  | Hospital |  |  | 0.52
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.57
|  |  | Multifamily |  |  | 0.57
|  |  | Office - Large |  |  | 0.6
|  |  | Office - Small |  |  | 0.4
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0.44
|  |  | Retail - Large |  |  | 0.43
|  |  | Retail - Small |  |  | 0.46
|  |  | Warehouse |  |  | 0.44
|  |  | Nonresidential Average |  |  | 0.43
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.19
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.14
|  |  | Health |  |  | 0.24
|  |  | Hospital |  |  | 0.22
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.25
|  |  | Multifamily |  |  | 0.25
|  |  | Office - Large |  |  | 0.26
|  |  | Office - Small |  |  | 0.17
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0.19
|  |  | Retail - Large |  |  | 0.19
|  |  | Retail - Small |  |  | 0.2
|  |  | Warehouse |  |  | 0.19
|  |  | Nonresidential Average |  |  | 0.19
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.67
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.22
|  |  | Health |  |  | 1.54
|  |  | Hospital |  |  | 1.53
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.15
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.24
|  |  | Office - Small |  |  | 1.45
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.39
|  |  | Retail - Large |  |  | 1.34
|  |  | Retail - Small |  |  | 1.39
|  |  | Warehouse |  |  | 1.43
|  |  | Nonresidential Average |  |  | 1.42
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 62.3%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 96.1%
|  |  | Hospital |  |  | 100%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 19.8%
|  |  | Multifamily |  |  | 19.8%
|  |  | Office - Large |  |  | 48.4%
|  |  | Office - Small |  |  | 63.6%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 96.7%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 71.7%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.018
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.014
|  |  | Health |  |  | 0.047
|  |  | Hospital |  |  | 0.022
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.024
|  |  | Multifamily |  |  | 0.024
|  |  | Office - Large |  |  | 0.026
|  |  | Office - Small |  |  | 0.017
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0.019
|  |  | Retail - Large |  |  | 0.018
|  |  | Retail - Small |  |  | 0.019
|  |  | Warehouse |  |  | 0.019
|  |  | Nonresidential Average |  |  | 0.018
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## HP and RW T8
HP and RW T8
| Measure Code: | NR-LTG-HPT8-V01-170101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) | 15
|  | 2-Lamp 32w HPT8 (BF < 0.77) | 17.5
|  | 3-Lamp 32w HPT8 (BF < 0.76) | 20
|  | 4-Lamp 32w HPT8 (BF < 0.78) | 22.5
|  | 6-Lamp 32w HPT8 (BF < 0.76) | 40
|  | 1-Lamp 28w RWT8 (BF < 0.76) | 15
|  | 2-Lamp 28w RWT8 (BF < 0.76) | 17.5
|  | 3-Lamp 28w RWT8 (BF < 0.77) | 20
|  | 4-Lamp 28w RWT8 (BF < 0.79) | 22.5
|  | 6-Lamp 28w RWT8 (BF < 0.77) | 40
| O&M Cost: | Please see reference tables in 3.4.7
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR] * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF] * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms]) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
| [MidLifeAdj] |  |  | =(([WattsT8base] -[WattsEE])/([WattsBase] - [WattsEE]))
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 30.1 | N | Watts | Input wattage of the existing or baseline system.
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 59.5
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 96.2
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 128.3
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 192.5
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 30.1
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 59.5
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 96.2
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 128.3
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 192.5
| [WattsEE] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 24 | N | Watts | Input wattage of the existing or baseline system.
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 48
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 71
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 98
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 142
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 21
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 43
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 63
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 88
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 126
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Education |  |  | 1.15
|  |  | Grocery |  |  | 1.14
|  |  | Health |  |  | 1.18
|  |  | Hospital |  |  | 1.24
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.1
|  |  | Multifamily |  |  | 1.1
|  |  | Office - Large |  |  | 1.13
|  |  | Office - Small |  |  | 1.15
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1.16
|  |  | Retail - Large |  |  | 1.14
|  |  | Retail - Small |  |  | 1.12
|  |  | Warehouse |  |  | 1.09
|  |  | Nonresidential Average |  |  | 1.13
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] |  |  |  |  | 100% | N |  | In Servce Rate or the percentage of units rebated that get installed
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.43
|  |  | Grocery |  |  | 0.32
|  |  | Health |  |  | 0.55
|  |  | Hospital |  |  | 0.52
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.57
|  |  | Multifamily |  |  | 0.57
|  |  | Office - Large |  |  | 0.6
|  |  | Office - Small |  |  | 0.4
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0.44
|  |  | Retail - Large |  |  | 0.43
|  |  | Retail - Small |  |  | 0.46
|  |  | Warehouse |  |  | 0.44
|  |  | Nonresidential Average |  |  | 0.43
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.14
|  |  | Health |  |  | 0.24
|  |  | Hospital |  |  | 0.22
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.25
|  |  | Multifamily |  |  | 0.25
|  |  | Office - Large |  |  | 0.26
|  |  | Office - Small |  |  | 0.17
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0.19
|  |  | Retail - Large |  |  | 0.19
|  |  | Retail - Small |  |  | 0.2
|  |  | Warehouse |  |  | 0.19
|  |  | Nonresidential Average |  |  | 0.19
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [MidLifeAdj] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 84% | C |  | A midlife savings adjustment should be applied to any measure with a blended T12:Standard T8 baseline. The adjustment should occur in 2020 to account for the baseline lamp replacement assumption changing from a blended 50/50 Standard T8/T12 to 100% Standard T8 by 2020.
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 78%
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 53%
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 48%
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 53%
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 89%
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 85%
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 65%
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 61%
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 65%
| [WattsT8Base] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 29 | N |  | Input wattage of the existing system based on 100% T8 fixture
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 57
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 84
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 113
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 169
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 29
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 57
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 84
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 113
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 169
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.67
|  |  | Grocery |  |  | 1.22
|  |  | Health |  |  | 1.54
|  |  | Hospital |  |  | 1.53
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.15
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.24
|  |  | Office - Small |  |  | 1.45
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.39
|  |  | Retail - Large |  |  | 1.34
|  |  | Retail - Small |  |  | 1.39
|  |  | Warehouse |  |  | 1.43
|  |  | Nonresidential Average |  |  | 1.42
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 100% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 62.3%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 96.1%
|  |  | Hospital |  |  | 100%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 19.8%
|  |  | Multifamily |  |  | 19.8%
|  |  | Office - Large |  |  | 48.4%
|  |  | Office - Small |  |  | 63.6%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 96.7%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 71.7%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.018
|  |  | Grocery |  |  | 0.014
|  |  | Health |  |  | 0.047
|  |  | Hospital |  |  | 0.022
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.024
|  |  | Multifamily |  |  | 0.024
|  |  | Office - Large |  |  | 0.026
|  |  | Office - Small |  |  | 0.017
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0.019
|  |  | Retail - Large |  |  | 0.018
|  |  | Retail - Small |  |  | 0.019
|  |  | Warehouse |  |  | 0.019
|  |  | Nonresidential Average |  |  | 0.018
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Occupancy Sensor
Occupancy Sensor
| Measure Code: | NR-LTG-OSLC-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
8
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Type | Full cost of switch (wall) mounted occupancy sensor (interior) |  | 54
|  | Full cost of fixture (bi-level) mounted occupancy sensor |  | 67
|  | Full cost of remote (ceiling) mounted occupancy sensor |  | 105
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [kW_Controlled] *[Hours] * [ESF] * [WHFe]
| Time of Sale Demand (ΔkW) | = [kW_Controlled] * [WHFd] * ([Cfbaseline] – [Cfos])
| Time of Sale Gas (ΔTherms) | = [kW_Controlled] * [Hours] * [ESF] * - [IFTherms]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [Heatdays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWControlled] | Lighting Control Type Interior | Switch (wall) mounted occupancy sensor |  |  | 0.304 | Y |  | Total lighting load connected to the control in kilowatts. Savings is per control. The total connected load per control should be collected from the customer, or use the default values presented
|  |  | Fixture-mounted occupancy sensor |  |  | 0.18
|  |  | Remote (ceiling) mounted occupancy sensor |  |  | 0.517
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [ESF] | Lighting Control Type Interior | Switch (wall) mounted occupancy sensor |  |  | 24% | Y |  | Energy Savings factor (represents the percentage reduction to the operating Hours from the non-controlled baseline lighting system). Determined on a site-specific basis or using the default values
|  |  | Fixture-mounted occupancy sensor |  |  | 24%
|  |  | Remote (ceiling) mounted occupancy sensor |  |  | 24%
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.15
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 1.14
|  |  | Health |  |  | 1.18
|  |  | Hospital |  |  | 1.24
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.1
|  |  | Multifamily |  |  | 1.1
|  |  | Office - Large |  |  | 1.13
|  |  | Office - Small |  |  | 1.15
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1.16
|  |  | Retail - Large |  |  | 1.14
|  |  | Retail - Small |  |  | 1.12
|  |  | Warehouse |  |  | 1.09
|  |  | Nonresidential Average |  |  | 1.13
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.43
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.32
|  |  | Health |  |  | 0.55
|  |  | Hospital |  |  | 0.52
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.57
|  |  | Multifamily |  |  | 0.57
|  |  | Office - Large |  |  | 0.6
|  |  | Office - Small |  |  | 0.4
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0.44
|  |  | Retail - Large |  |  | 0.43
|  |  | Retail - Small |  |  | 0.46
|  |  | Warehouse |  |  | 0.44
|  |  | Nonresidential Average |  |  | 0.43
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.19
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.14
|  |  | Health |  |  | 0.24
|  |  | Hospital |  |  | 0.22
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.25
|  |  | Multifamily |  |  | 0.25
|  |  | Office - Large |  |  | 0.26
|  |  | Office - Small |  |  | 0.17
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0.19
|  |  | Retail - Large |  |  | 0.19
|  |  | Retail - Small |  |  | 0.2
|  |  | Warehouse |  |  | 0.19
|  |  | Nonresidential Average |  |  | 0.19
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.67
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.22
|  |  | Health |  |  | 1.54
|  |  | Hospital |  |  | 1.53
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.15
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.24
|  |  | Office - Small |  |  | 1.45
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.39
|  |  | Retail - Large |  |  | 1.34
|  |  | Retail - Small |  |  | 1.39
|  |  | Warehouse |  |  | 1.43
|  |  | Nonresidential Average |  |  | 1.42
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CFbaseline] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Baseline Summer Peak Coincidence Factor for the lighting system without Occupancy Sensors installed is selected from the Lighting Reference Table in Section 3.4 for each building type. If the building type is unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 62.3%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 96.1%
|  |  | Hospital |  |  | 100%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 19.8%
|  |  | Multifamily |  |  | 19.8%
|  |  | Office - Large |  |  | 48.4%
|  |  | Office - Small |  |  | 63.6%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 96.7%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 71.7%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [CFos] |  |  |  |  | 0.15 | N |  | Retrofit Summer Peak Coincidence Factor the lighting system with Occupancy Sensors installed
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.018
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.014
|  |  | Health |  |  | 0.047
|  |  | Hospital |  |  | 0.022
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.024
|  |  | Multifamily |  |  | 0.024
|  |  | Office - Large |  |  | 0.026
|  |  | Office - Small |  |  | 0.017
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0.019
|  |  | Retail - Large |  |  | 0.018
|  |  | Retail - Small |  |  | 0.019
|  |  | Warehouse |  |  | 0.019
|  |  | Nonresidential Average |  |  | 0.018
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## VFDs for Process
VFDs for Process
| Measure Code: | NR-MSC-VFDP-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  | Actual - Baseline | Actual
|  | Unknown | Horse Power | 1-9 | 1874
|  |  |  | 10-19 | 2967
|  |  |  | 20-29 | 4060
|  |  |  | 30-39 | 5154
|  |  |  | 40-49 | 6247
|  |  |  | 50-59 | 7340
|  |  |  | 60-69 | 8433
|  |  |  | 70-75 | 9526
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [HP] * [Hours] * [SF]
| Time of Sale Demand (ΔkW) | Custom Calculation Required
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [HP] | [5 empty] | Y | HP | Nominal horsepower of controlled motor
| [HOURS] | [5 empty] | Y | Hours | Annual operating hours of motor
| [SF] | Type | Process Fans |  |  | 0.189 | N | kWh/HP | Savings factor
|  |  | Process Centrifugal Pumps |  |  | 0.26